## index
Item | Sheet Number
Main Switch | 1
Change Over Switch | 2
VTPN | 3
MCB | 4
MCCB | 5
SPN DB | 6
MCB Isolator | 7
HTPN | 8
Cable | 9
Laying | 10
ACB | 11
Point Switch Board | 12
On Board | 13
Avg. 5A Switch Board | 14
End box for TPN SFU | 15
Main Switch Open | 16
Change Over Switch Open | 17
End box for Vertical TPN DB | 18
End box for Horizontal TPN DB | 19
Compression Glands | 20
Wiring | 21
Current Capacity of Aluminium Cable | 22
Current Capacity of Copper Cable | 23
Current Capacity of Copper Wire | 24
Approximate Mili Voltage drop per ampere per metre - Aluminium | 25
Approximate Mili Voltage drop per ampere per metre - Copper | 26

## 1
Item | Type | Enclosure | Mounting | Current Rating | Voltage | Company | Rate | Description | GS
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 32A | 415V - TPN | Siemens | 3904 | Supplying and fixing following TPN SFU with sheet steel enclosure on flat iron frame on wall with nuts bolts etc incl. S & F 3 nos. DIN type HRC fuse as per rating | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 32A | 415V - TPN | L&T | 3071 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 32A | 415V - TPN | Havells | 2370 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 32A | 415V - TPN | Standard | 1890 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 50A | 415V - TPN | Siemens | 4387 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 63A | 415V - TPN | L&T | 4038 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 63A | 415V - TPN | Havells | 2998 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 63A | 415V - TPN | Standard | 2453 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 80A | 415V - TPN | Siemens | 6060 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 100A | 415V - TPN | Siemens | 7245 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 100A | 415V - TPN | L&T | 6229 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 100A | 415V - TPN | Havells | 5588 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 100A | 415V - TPN | Standard | 4564 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 125A | 415V - TPN | Siemens | 8830 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 125A | 415V - TPN | L&T | 7321 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 125A | 415V - TPN | Havells | 6140 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 125A | 415V - TPN | Standard | 4918 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 160A | 415V - TPN | Siemens | 9412 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 160A | 415V - TPN | L&T | 7908 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 160A | 415V - TPN | Havells | 7728 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 160A | 415V - TPN | Standard | 5493 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 200A | 415V - TPN | Siemens | 12230 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 200A | 415V - TPN | L&T | 10306 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 200A | 415V - TPN | Havells | 8741 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 250A | 415V - TPN | Siemens | 13944 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 250A | 415V - TPN | L&T | 11920 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 250A | 415V - TPN | Havells | 9629 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 250A | 415V - TPN | Standard | 7846 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 315A | 415V - TPN | Siemens | 16800 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 315A | 415V - TPN | L&T | 13856 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 315A | 415V - TPN | Havells | 12359 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 315A | 415V - TPN | Standard | 9796 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 415A | 415V - TPN | Siemens | 19424 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 415A | 415V - TPN | L&T | 16357 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 415A | 415V - TPN | Havells | 15075 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Flat Iron frame | 415A | 415V - TPN | Standard | 12001 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 32A | 415V - TPN | Siemens | 3998 | Supplying and fixing following TPN SFU with sheet steel enclosure on angle iron frame on wall with nuts bolts etc incl. S & F 3 nos. DIN type HRC fuse as per rating | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 32A | 415V - TPN | L&T | 3165 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 32A | 415V - TPN | Havells | 2464 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 32A | 415V - TPN | Standard | 1984 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 50A | 415V - TPN | Siemens | 4481 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 63A | 415V - TPN | L&T | 4132 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 63A | 415V - TPN | Havells | 3092 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 63A | 415V - TPN | Standard | 2547 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 80A | 415V - TPN | Siemens | 6154 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 100A | 415V - TPN | Siemens | 7339 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 100A | 415V - TPN | L&T | 6323 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 100A | 415V - TPN | Havells | 5682 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 100A | 415V - TPN | Standard | 4658 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 125A | 415V - TPN | Siemens | 8924 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 125A | 415V - TPN | L&T | 7415 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 125A | 415V - TPN | Havells | 6234 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 125A | 415V - TPN | Standard | 5012 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 160A | 415V - TPN | Siemens | 9506 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 160A | 415V - TPN | L&T | 8002 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 160A | 415V - TPN | Havells | 7822 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 160A | 415V - TPN | Standard | 5587 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 200A | 415V - TPN | Siemens | 12324 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 200A | 415V - TPN | L&T | 10400 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 200A | 415V - TPN | Havells | 8835 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 250A | 415V - TPN | Siemens | 14038 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 250A | 415V - TPN | L&T | 12014 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 250A | 415V - TPN | Havells | 9723 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 250A | 415V - TPN | Standard | 7940 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 315A | 415V - TPN | Siemens | 16894 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 315A | 415V - TPN | L&T | 13950 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 315A | 415V - TPN | Havells | 12453 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 315A | 415V - TPN | Standard | 9890 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 415A | 415V - TPN | Siemens | 24013 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 415A | 415V - TPN | L&T | 16451 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 415A | 415V - TPN | Havells | 15169 |  | PWD/GS -D-3 : 4(a)
Main Switch | TPN SFU | Sheet steel enclosure | Angle iron frame | 415A | 415V - TPN | Standard | 12095 |  | PWD/GS -D-3 : 4(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 16 A | 240V - DP | Standard | 519 | Supplying and fixing following Sheet steel Main Switches on flat iron frame on wall | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 16 A | 240V - DP | Havells | 576 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 16 A | 240V - DP | HPL | 577 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 16 A | 240V - DP | Anchor | 445 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 16 A | 415V - TPN | Standard | 1231 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 16 A | 415V - TPN | Havells | 1399 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 16 A | 415V - TPN | HPL | 1400 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 16 A | 415V - TPN | Anchor | 743 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 32 A | 240V - DP | Standard | 1128 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 32 A | 240V - DP | Havells | 1277 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 32 A | 240V - DP | HPL | 1228 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 32 A | 240V - DP | Anchor | 705 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 32 A | 415V - TPN | Standard | 1593 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 32 A | 415V - TPN | Havells | 1738 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 32 A | 415V - TPN | HPL | 1743 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Flat Iron frame | 32 A | 415V - TPN | Anchor | 938 |  | PWD/GS -D-1 : 1(a)
Main Switch | Normal | Sheet steel | Angle iron frame | 63 A | 415V - TPN | Standard | 3180 | Supplying and fixing following Sheet steel Main Switches on Angle iron frame on wall | PWD/GS -D-1 : 1(b)
Main Switch | Normal | Sheet steel | Angle iron frame | 63 A | 415V - TPN | Havells | 3568 |  | PWD/GS -D-1 : 1(b)
Main Switch | Normal | Sheet steel | Angle iron frame | 63 A | 415V - TPN | HPL | 3569 |  | PWD/GS -D-1 : 1(b)
Main Switch | Normal | Sheet steel | Angle iron frame | 63 A | 415V - TPN | Anchor | 2631 |  | PWD/GS -D-1 : 1(b)
Main Switch | Normal | Sheet steel | Angle iron frame | 125 A | 415V - TPN | Standard | 5503 |  | PWD/GS -D-1 : 1(b)
Main Switch | Normal | Sheet steel | Angle iron frame | 125 A | 415V - TPN | Havells | 6448 |  | PWD/GS -D-1 : 1(b)
Main Switch | Normal | Sheet steel | Angle iron frame | 125 A | 415V - TPN | HPL | 6450 |  | PWD/GS -D-1 : 1(b)
Main Switch | Normal | Sheet steel | Angle iron frame | 125 A | 415V - TPN | Anchor | 4223 |  | PWD/GS -D-1 : 1(b)

## 2
Item | Type | Mounting | Current Rating | Voltage | Company | Rate | Description | GS
Change Over Switch | Sheet Steel enclosure | flat iron frame | 16A | 415V FP | HPL | 1989 | Supplying and fixing following Changeover switch with Sheet Steel enclosure on flat iron frame on wall with nuts bolts etc | PWD/GS -D-1 : 2(a)
Change Over Switch | Sheet Steel enclosure | flat iron frame | 16A | 415V FP | Havells | 1989 |  | PWD/GS -D-1 : 2(a)
Change Over Switch | Sheet Steel enclosure | flat iron frame | 16A | 415V FP | Standard | 1856 |  | PWD/GS -D-1 : 2(a)
Change Over Switch | Sheet Steel enclosure | flat iron frame | 32A | 240V DP | HPL | 1441 |  | PWD/GS -D-1 : 2(a)
Change Over Switch | Sheet Steel enclosure | flat iron frame | 32A | 240V DP | Havells | 1403 |  | PWD/GS -D-1 : 2(a)
Change Over Switch | Sheet Steel enclosure | flat iron frame | 32A | 240V DP | Standard | 1315 |  | PWD/GS -D-1 : 2(a)
Change Over Switch | Sheet Steel enclosure | flat iron frame | 32A | 415V FP | HPL | 2366 |  | PWD/GS -D-1 : 2(a)
Change Over Switch | Sheet Steel enclosure | flat iron frame | 32A | 415V FP | Havells | 2362 |  | PWD/GS -D-1 : 2(a)
Change Over Switch | Sheet Steel enclosure | flat iron frame | 32A | 415V FP | Standard | 2126 |  | PWD/GS -D-1 : 2(a)
Change Over Switch | Sheet Steel enclosure | flat iron frame | 63A | 240V DP | HPL | 2627 |  | PWD/GS -D-1 : 2(a)
Change Over Switch | Sheet Steel enclosure | flat iron frame | 63A | 240V DP | Havells | 2545 |  | PWD/GS -D-1 : 2(a)
Change Over Switch | Sheet Steel enclosure | flat iron frame | 63A | 240V DP | Standard | 2431 |  | PWD/GS -D-1 : 2(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 63A | 415V FP | HPL | 4763 | Supplying and fixing following Changeover switch with Sheet Steel enclosure on angle iron frame on wall with nuts bolts etc | PWD/GS -D-1 : 2(b)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 63A | 415V FP | Havells | 4760 |  | PWD/GS -D-1 : 2(b)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 63A | 415V FP | Standard | 4349 |  | PWD/GS -D-1 : 2(b)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 100A | 415V FP | HPL | 9322 |  | PWD/GS -D-1 : 2(b)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 100A | 415V FP | Havells | 9323 |  | PWD/GS -D-1 : 2(b)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 100A | 415V FP | Standard | 8454 |  | PWD/GS -D-1 : 2(b)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 125A | 415V FP | L&T | 8568 | Supplying and fixing follwoing on load front operated Changeover switch with Sheet Steel enclosure on angle iron frame on wall with nuts bolts etc | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 125A | 415V FP | Havells | 9704 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 125A | 415V FP | HPL | 9501 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 125A | 415V FP | Standard | 9429 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 160A | 415V FP | L&T | 9395 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 160A | 415V FP | Havells | 10035 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 160A | 415V FP | HPL | 10399 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 160A | 415V FP | Standard | 9749 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 200A | 415V FP | L&T | 10542 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 200A | 415V FP | Havells | 11649 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 200A | 415V FP | HPL | 11968 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 200A | 415V FP | Standard | 11319 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 250A | 415V FP | L&T | 14891 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 250A | 415V FP | Havells | 15512 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 250A | 415V FP | HPL | 16554 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 250A | 415V FP | Standard | 15066 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 320A | 415V FP | L&T | 15588 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 320A | 415V FP | Havells | 16170 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 320A | 415V FP | HPL | 17308 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 320A | 415V FP | Standard | 15569 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 415A | 415V FP | L&T | 22751 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 415A | 415V FP | Havells | 24286 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 415A | 415V FP | HPL | 25205 |  | PWD/GS -D-2 : 3(a)
Change Over Switch | Sheet Steel enclosure | angle iron frame | 415A | 415V FP | Standard | 23586 |  | PWD/GS -D-2 : 3(a)

## 3
Item | Current Rating | Way | Company | Rate | Description | GS
VTPN | Up to 100A | 4 way | Schneider | 6677 | Supplying and fixing following double door Vertical TPN MCB Distribution board for MCCB incomer with IP-42/43 protection, on angle iron frame on wall & mending good the damages to original finish incl. Inter connection with suitable size of copper wire and neutral link & provision for earthing attachment | PWD/GS -D-11 : 15
VTPN | Up to 100A | 8 way | Schneider | 7786
VTPN | Up to 100A | 12 way | Schneider | 9961
VTPN | Up to 160A | 4 way | Legrand | 8627
VTPN | Up to 160A | 8 way | Legrand | 10683
VTPN | Up to 160A | 12 way | Legrand | 14020
VTPN | Up to 160A | 4 way | Schneider | 8456
VTPN | Up to 160A | 8 way | Schneider | 10372
VTPN | Up to 160A | 12 way | Schneider | 13605
VTPN | Up to 160A | 4 way | Crabtree | 7687
VTPN | Up to 160A | 8 way | Crabtree | 8631
VTPN | Up to 160A | 12 way | Crabtree | 10695
VTPN | Up to 160A | 4 way | Siemens | 6601
VTPN | Up to 160A | 6 way | Siemens | 8163
VTPN | Up to 160A | 8 way | Siemens | 8761
VTPN | Up to 160A | 12 way | Siemens | 11480
VTPN | Up to 160A | 4 way | ABB | 6644
VTPN | Up to 160A | 6 way | ABB | 7717
VTPN | Up to 160A | 8 way | ABB | 8281
VTPN | Up to 160A | 12 way | ABB | 10840
VTPN | Up to 160A | 4 way | L&T | 8064
VTPN | Up to 160A | 6 way | L&T | 9100
VTPN | Up to 160A | 8 way | L&T | 10006
VTPN | Up to 160A | 12 way | L&T | 12779
VTPN | Up to 250A | 4 way | Legrand | 15386
VTPN | Up to 250A | 8 way | Legrand | 17947
VTPN | Up to 250A | 12 way | Legrand | 18883
VTPN | Up to 250A | 8 way | Schneider | 17409
VTPN | Up to 250A | 12 way | Schneider | 17409
VTPN | Up to 250A | 4 way | ABB | 12014
VTPN | Up to 250A | 6 way | ABB | 13131
VTPN | Up to 250A | 8 way | ABB | 14034
VTPN | Up to 250A | 12 way | ABB | 14629

## 4
Item | Current Rating | Pole | Company | Rate | Description | GS
MCB | 6 A | SP | Legrand | 190 | Supplying and fixing following 240/415 V MCB of Breaking capacity 10kA & C characteristics on din rail of existing DBs and necessary connection | PWD/GS -D-6:7
MCB | 10 A | SP | Legrand | 190
MCB | 16 A | SP | Legrand | 190
MCB | 20 A | SP | Legrand | 190
MCB | 25 A | SP | Legrand | 190
MCB | 32 A | SP | Legrand | 190
MCB | 40 A | SP | Legrand | 422
MCB | 63 A | SP | Legrand | 422
MCB | 6 A | DP | Legrand | 546
MCB | 10 A | DP | Legrand | 546
MCB | 16 A | DP | Legrand | 546
MCB | 20 A | DP | Legrand | 546
MCB | 25 A | DP | Legrand | 546
MCB | 32 A | DP | Legrand | 546
MCB | 40 A | DP | Legrand | 938
MCB | 63 A | DP | Legrand | 938
MCB | 6 A | TP | Legrand | 546
MCB | 10 A | TP | Legrand | 546
MCB | 16 A | TP | Legrand | 546
MCB | 20 A | TP | Legrand | 546
MCB | 25 A | TP | Legrand | 546
MCB | 32 A | TP | Legrand | 546
MCB | 40 A | TP | Legrand | 1432
MCB | 63 A | TP | Legrand | 1432
MCB | 100 A | TP | Legrand | 5348
MCB | 125 A | TP | Legrand | 5932
MCB | 6 A | FP | Legrand | 1196
MCB | 10 A | FP | Legrand | 1196
MCB | 16 A | FP | Legrand | 1196
MCB | 20 A | FP | Legrand | 1196
MCB | 25 A | FP | Legrand | 1196
MCB | 32 A | FP | Legrand | 1196
MCB | 40 A | FP | Legrand | 1830
MCB | 63 A | FP | Legrand | 1830
MCB | 100 A | FP | Legrand | 6815
MCB | 125 A | FP | Legrand | 7708
MCB | 6 A | SP | Schneider | 157
MCB | 10 A | SP | Schneider | 157
MCB | 16 A | SP | Schneider | 157
MCB | 20 A | SP | Schneider | 157
MCB | 25 A | SP | Schneider | 157
MCB | 32 A | SP | Schneider | 157
MCB | 40 A | SP | Schneider | 318
MCB | 63 A | SP | Schneider | 365
MCB | 6 A | DP | Schneider | 473
MCB | 10 A | DP | Schneider | 473
MCB | 16 A | DP | Schneider | 473
MCB | 20 A | DP | Schneider | 473
MCB | 25 A | DP | Schneider | 473
MCB | 32 A | DP | Schneider | 473
MCB | 40 A | DP | Schneider | 692
MCB | 63 A | DP | Schneider | 791
MCB | 6 A | TP | Schneider | 734
MCB | 10 A | TP | Schneider | 734
MCB | 16 A | TP | Schneider | 734
MCB | 20 A | TP | Schneider | 734
MCB | 25 A | TP | Schneider | 734
MCB | 32 A | TP | Schneider | 734
MCB | 40 A | TP | Schneider | 1070
MCB | 63 A | TP | Schneider | 1142
MCB | 100 A | TP | Schneider | 6425
MCB | 125 A | TP | Schneider | 6920
MCB | 6 A | FP | Schneider | 1027
MCB | 10 A | FP | Schneider | 1027
MCB | 16 A | FP | Schneider | 1027
MCB | 20 A | FP | Schneider | 1027
MCB | 25 A | FP | Schneider | 1027
MCB | 32 A | FP | Schneider | 1027
MCB | 40 A | FP | Schneider | 1373
MCB | 63 A | FP | Schneider | 1468
MCB | 100 A | FP | Schneider | 8179
MCB | 125 A | FP | Schneider | 8868
MCB | 6 A | SP | Crabtree | 176
MCB | 10 A | SP | Crabtree | 176
MCB | 16 A | SP | Crabtree | 176
MCB | 20 A | SP | Crabtree | 176
MCB | 25 A | SP | Crabtree | 176
MCB | 32 A | SP | Crabtree | 176
MCB | 40 A | SP | Crabtree | 378
MCB | 63 A | SP | Crabtree | 435
MCB | 6 A | DP | Crabtree | 558
MCB | 10 A | DP | Crabtree | 558
MCB | 16 A | DP | Crabtree | 558
MCB | 20 A | DP | Crabtree | 558
MCB | 25 A | DP | Crabtree | 558
MCB | 32 A | DP | Crabtree | 558
MCB | 40 A | DP | Crabtree | 821
MCB | 63 A | DP | Crabtree | 966
MCB | 6 A | TP | Crabtree | 850
MCB | 10 A | TP | Crabtree | 850
MCB | 16 A | TP | Crabtree | 850
MCB | 20 A | TP | Crabtree | 850
MCB | 25 A | TP | Crabtree | 850
MCB | 32 A | TP | Crabtree | 850
MCB | 40 A | TP | Crabtree | 1227
MCB | 63 A | TP | Crabtree | 1383
MCB | 100 A | TP | Crabtree | 4625
MCB | 125 A | TP | Crabtree | 5203
MCB | 6 A | FP | Crabtree | 1213
MCB | 10 A | FP | Crabtree | 1213
MCB | 16 A | FP | Crabtree | 1213
MCB | 20 A | FP | Crabtree | 1213
MCB | 25 A | FP | Crabtree | 1213
MCB | 32 A | FP | Crabtree | 1213
MCB | 40 A | FP | Crabtree | 1647
MCB | 63 A | FP | Crabtree | 1817
MCB | 100 A | FP | Crabtree | 5993
MCB | 125 A | FP | Crabtree | 6343
MCB | 6 A | SP | Siemens | 184
MCB | 10 A | SP | Siemens | 184
MCB | 16 A | SP | Siemens | 184
MCB | 20 A | SP | Siemens | 184
MCB | 25 A | SP | Siemens | 184
MCB | 32 A | SP | Siemens | 184
MCB | 40 A | SP | Siemens | 371
MCB | 63 A | SP | Siemens | 393
MCB | 6 A | DP | Siemens | 520
MCB | 10 A | DP | Siemens | 520
MCB | 16 A | DP | Siemens | 520
MCB | 20 A | DP | Siemens | 520
MCB | 25 A | DP | Siemens | 520
MCB | 32 A | DP | Siemens | 520
MCB | 40 A | DP | Siemens | 844
MCB | 63 A | DP | Siemens | 886
MCB | 6 A | TP | Siemens | 846
MCB | 10 A | TP | Siemens | 846
MCB | 16 A | TP | Siemens | 846
MCB | 20 A | TP | Siemens | 846
MCB | 25 A | TP | Siemens | 846
MCB | 32 A | TP | Siemens | 846
MCB | 40 A | TP | Siemens | 1280
MCB | 63 A | TP | Siemens | 1343
MCB | 6 A | FP | Siemens | 1106
MCB | 10 A | FP | Siemens | 1106
MCB | 16 A | FP | Siemens | 1106
MCB | 20 A | FP | Siemens | 1106
MCB | 25 A | FP | Siemens | 1106
MCB | 32 A | FP | Siemens | 1106
MCB | 40 A | FP | Siemens | 1655
MCB | 63 A | FP | Siemens | 1737
MCB | 6 A | SP | ABB | 171
MCB | 10 A | SP | ABB | 171
MCB | 16 A | SP | ABB | 171
MCB | 20 A | SP | ABB | 171
MCB | 25 A | SP | ABB | 171
MCB | 32 A | SP | ABB | 171
MCB | 40 A | SP | ABB | 347
MCB | 63 A | SP | ABB | 352
MCB | 6 A | DP | ABB | 492
MCB | 10 A | DP | ABB | 492
MCB | 16 A | DP | ABB | 492
MCB | 20 A | DP | ABB | 492
MCB | 25 A | DP | ABB | 492
MCB | 32 A | DP | ABB | 492
MCB | 40 A | DP | ABB | 783
MCB | 63 A | DP | ABB | 791
MCB | 6 A | TP | ABB | 793
MCB | 10 A | TP | ABB | 793
MCB | 16 A | TP | ABB | 793
MCB | 20 A | TP | ABB | 793
MCB | 25 A | TP | ABB | 793
MCB | 32 A | TP | ABB | 793
MCB | 40 A | TP | ABB | 1212
MCB | 63 A | TP | ABB | 1219
MCB | 100 A | TP | ABB | 5287
MCB | 125 A | TP | ABB | 5443
MCB | 6 A | FP | ABB | 1061
MCB | 10 A | FP | ABB | 1061
MCB | 16 A | FP | ABB | 1061
MCB | 20 A | FP | ABB | 1061
MCB | 25 A | FP | ABB | 1061
MCB | 32 A | FP | ABB | 1061
MCB | 40 A | FP | ABB | 1556
MCB | 63 A | FP | ABB | 1563
MCB | 100 A | FP | ABB | 7177
MCB | 125 A | FP | ABB | 7261
MCB | 6 A | SP | L&T | 160
MCB | 10 A | SP | L&T | 160
MCB | 16 A | SP | L&T | 160
MCB | 20 A | SP | L&T | 160
MCB | 25 A | SP | L&T | 160
MCB | 32 A | SP | L&T | 160
MCB | 40 A | SP | L&T | 371
MCB | 63 A | SP | L&T | 371
MCB | 6 A | DP | L&T | 478
MCB | 10 A | DP | L&T | 478
MCB | 16 A | DP | L&T | 478
MCB | 20 A | DP | L&T | 478
MCB | 25 A | DP | L&T | 478
MCB | 32 A | DP | L&T | 478
MCB | 40 A | DP | L&T | 814
MCB | 63 A | DP | L&T | 814
MCB | 6 A | TP | L&T | 770
MCB | 10 A | TP | L&T | 770
MCB | 16 A | TP | L&T | 770
MCB | 20 A | TP | L&T | 770
MCB | 25 A | TP | L&T | 770
MCB | 32 A | TP | L&T | 770
MCB | 40 A | TP | L&T | 1189
MCB | 63 A | TP | L&T | 1189
MCB | 6 A | FP | L&T | 1046
MCB | 10 A | FP | L&T | 1046
MCB | 16 A | FP | L&T | 1046
MCB | 20 A | FP | L&T | 1046
MCB | 25 A | FP | L&T | 1046
MCB | 32 A | FP | L&T | 1046
MCB | 40 A | FP | L&T | 1525
MCB | 63 A | FP | L&T | 1525
MCB | 6 A | SP | Havells | 168
MCB | 10 A | SP | Havells | 168
MCB | 16 A | SP | Havells | 168
MCB | 20 A | SP | Havells | 168
MCB | 25 A | SP | Havells | 168
MCB | 32 A | SP | Havells | 168
MCB | 40 A | SP | Havells | 328
MCB | 63 A | SP | Havells | 360
MCB | 6 A | DP | Havells | 478
MCB | 10 A | DP | Havells | 478
MCB | 16 A | DP | Havells | 478
MCB | 20 A | DP | Havells | 478
MCB | 25 A | DP | Havells | 478
MCB | 32 A | DP | Havells | 478
MCB | 40 A | DP | Havells | 703
MCB | 63 A | DP | Havells | 795
MCB | 6 A | TP | Havells | 747
MCB | 10 A | TP | Havells | 747
MCB | 16 A | TP | Havells | 747
MCB | 20 A | TP | Havells | 747
MCB | 25 A | TP | Havells | 747
MCB | 32 A | TP | Havells | 747
MCB | 40 A | TP | Havells | 1089
MCB | 63 A | TP | Havells | 1150
MCB | 100 A | TP | Havells | 4007
MCB | 125 A | TP | Havells | 4510
MCB | 6 A | FP | Havells | 1027
MCB | 10 A | FP | Havells | 1027
MCB | 16 A | FP | Havells | 1027
MCB | 20 A | FP | Havells | 1027
MCB | 25 A | FP | Havells | 1027
MCB | 32 A | FP | Havells | 1027
MCB | 40 A | FP | Havells | 1392
MCB | 63 A | FP | Havells | 1476
MCB | 100 A | FP | Havells | 5189
MCB | 125 A | FP | Havells | 5509
MCB | 6 A | SP | Standard | 146
MCB | 10 A | SP | Standard | 146
MCB | 16 A | SP | Standard | 146
MCB | 20 A | SP | Standard | 146
MCB | 25 A | SP | Standard | 146
MCB | 32 A | SP | Standard | 146
MCB | 40 A | SP | Standard | 305
MCB | 63 A | SP | Standard | 359
MCB | 6 A | DP | Standard | 471
MCB | 10 A | DP | Standard | 471
MCB | 16 A | DP | Standard | 471
MCB | 20 A | DP | Standard | 471
MCB | 25 A | DP | Standard | 471
MCB | 32 A | DP | Standard | 471
MCB | 40 A | DP | Standard | 658
MCB | 63 A | DP | Standard | 776
MCB | 6 A | TP | Standard | 708
MCB | 10 A | TP | Standard | 708
MCB | 16 A | TP | Standard | 708
MCB | 20 A | TP | Standard | 708
MCB | 25 A | TP | Standard | 708
MCB | 32 A | TP | Standard | 708
MCB | 40 A | TP | Standard | 1017
MCB | 63 A | TP | Standard | 1138
MCB | 100 A | TP | Standard | 3999
MCB | 125 A | TP | Standard | 4502
MCB | 6 A | FP | Standard | 1046
MCB | 10 A | FP | Standard | 1046
MCB | 16 A | FP | Standard | 1046
MCB | 20 A | FP | Standard | 1046
MCB | 25 A | FP | Standard | 1046
MCB | 32 A | FP | Standard | 1046
MCB | 40 A | FP | Standard | 1370
MCB | 63 A | FP | Standard | 1487
MCB | 100 A | FP | Standard | 5189
MCB | 125 A | FP | Standard | 5509

## 5
Item | Current Rating | Pole | Company | Rate | Description | GS
MCCB | 63 A | FP | Legrand | 7071 | Supplying and fixing following 415 V Four Pole MCCB of Breaking capacity 25kA/35kA with fixed thermal and fixed magnetic / adjustable thermal and fixed magnetic setting in existing DBs / enclosure and necessary connection | PWD/GS -D-8 : 10
MCCB | 80 A | FP | Legrand | 7071
MCCB | 100 A | FP | Legrand | 7143
MCCB | 125 A | FP | Legrand | 8139
MCCB | 160 A | FP | Legrand | 9759
MCCB | 200 A | FP | Legrand | 14798
MCCB | 250 A | FP | Legrand | 18486
MCCB | 63 A | FP | Schneider | 4934
MCCB | 80 A | FP | Schneider | 4934
MCCB | 100 A | FP | Schneider | 4934
MCCB | 125 A | FP | Schneider | 7032
MCCB | 160 A | FP | Schneider | 8784
MCCB | 200 A | FP | Schneider | 10886
MCCB | 250 A | FP | Schneider | 12897
MCCB | 63 A | FP | Siemens | 6236
MCCB | 80 A | FP | Siemens | 6236
MCCB | 100 A | FP | Siemens | 6236
MCCB | 125 A | FP | Siemens | 8441
MCCB | 160 A | FP | Siemens | 10547
MCCB | 63 A | FP | ABB | 3086
MCCB | 80 A | FP | ABB | 3088
MCCB | 100 A | FP | ABB | 3088
MCCB | 125 A | FP | ABB | 3239
MCCB | 160 A | FP | ABB | 6362
MCCB | 200 A | FP | ABB | 6362
MCCB | 250 A | FP | ABB | 7314
MCCB | 63 A | FP | L&T | 4267
MCCB | 80 A | FP | L&T | 4267
MCCB | 100 A | FP | L&T | 4267
MCCB | 125 A | FP | L&T | 5866
MCCB | 160 A | FP | L&T | 7292
MCCB | 200 A | FP | L&T | 10018
MCCB | 250 A | FP | L&T | 11693

## 6
Item | Way | Company | Rate | Description | GS
SPN DB | 2+8 way | Legrand | 1477 | Supplying and fixing following double-door SPN MCB Distribution Board with IP-42/43 protection, concealed in wall after cutting the wall & mending good the damages to original finish incl. Inter connection with suitable size of copper wire and neutral link & provision for earthing attachment. | PWD/GS -D-9:13
SPN DB | 2+4 way | Legrand | 1186 |  | PWD/GS -D-9:13
SPN DB | 2+12 way | Legrand | 1757
SPN DB | 2+16 way | Legrand | 2200
SPN DB | 2+6 way | Schneider | 1156
SPN DB | 2+8 way | Schneider | 1392
SPN DB | 2+12 way | Schneider | 1673
SPN DB | 2+18 way | Schneider | 2138
SPN DB | 2+2 way | Crabtree | 1111
SPN DB | 2+4 way | Crabtree | 1221
SPN DB | 2+6 way | Crabtree | 1346
SPN DB | 2+10 way | Crabtree | 1654
SPN DB | 2+14 way | Crabtree | 2199
SPN DB | 2+4 way | Siemens | 1293
SPN DB | 2+6 way | Siemens | 1335
SPN DB | 2+8 way | Siemens | 1563
SPN DB | 2+10 way | Siemens | 1601
SPN DB | 2+12 way | Siemens | 1851
SPN DB | 2+14 way | Siemens | 1917
SPN DB | 2+4 way | ABB | 1055
SPN DB | 2+6 way | ABB | 1155
SPN DB | 2+8 way | ABB | 1362
SPN DB | 2+10 way | ABB | 1383
SPN DB | 2+12 way | ABB | 1560
SPN DB | 2+14 way | ABB | 1708
SPN DB | 2+2 way | L&T | 978
SPN DB | 2+4 way | L&T | 1107
SPN DB | 2+6 way | L&T | 1202
SPN DB | 2+10 way | L&T | 1479
SPN DB | 2+14 way | L&T | 1795
SPN DB | 2+4 way | Havells | 935
SPN DB | 2+6 way | Havells | 1073
SPN DB | 2+8 way | Havells | 1197
SPN DB | 2+12 way | Havells | 1436
SPN DB | 2+16 way | Havells | 1894
SPN DB | 2+4 way | Standard | 870
SPN DB | 2+6 way | Standard | 1008
SPN DB | 2+8 way | Standard | 1098
SPN DB | 2+12 way | Standard | 1394
SPN DB | 2+16 way | Standard | 1720

## 7
Item | Current Rating | Pole | Company | Rate | Description | GS
MCB Isolator | 32 A | DP | Legrand | 322 | Supplying and fixing following 240/415 V MCB Isolator on din rail of existing DBs and necessary connection. | PWD/GS -D-6:6
MCB Isolator | 40 A | DP | Legrand | 349
MCB Isolator | 63 A | DP | Legrand | 460
MCB Isolator | 32 A | FP | Legrand | 624
MCB Isolator | 40 A | FP | Legrand | 773
MCB Isolator | 63 A | FP | Legrand | 845
MCB Isolator | 100A | FP | Legrand | 927
MCB Isolator | 125A | FP | Legrand | 1102
MCB Isolator | 40 A | DP | Schneider | 354
MCB Isolator | 63 A | DP | Schneider | 472
MCB Isolator | 40 A | FP | Schneider | 779
MCB Isolator | 63 A | FP | Schneider | 855
MCB Isolator | 80 A | FP | Schneider | 1194
MCB Isolator | 100A | FP | Schneider | 1213
MCB Isolator | 125A | FP | Schneider | 1277
MCB Isolator | 40 A | DP | Crabtree | 338
MCB Isolator | 63 A | DP | Crabtree | 436
MCB Isolator | 40 A | FP | Crabtree | 790
MCB Isolator | 63 A | FP | Crabtree | 801
MCB Isolator | 80 A | FP | Crabtree | 1011
MCB Isolator | 100A | FP | Crabtree | 1011
MCB Isolator | 125A | FP | Crabtree | 1095
MCB Isolator | 25 A | DP | Siemens | 322
MCB Isolator | 40 A | DP | Siemens | 338
MCB Isolator | 63 A | DP | Siemens | 402
MCB Isolator | 25 A | FP | Siemens | 611
MCB Isolator | 40 A | FP | Siemens | 710
MCB Isolator | 63 A | FP | Siemens | 760
MCB Isolator | 80 A | FP | Siemens | 881
MCB Isolator | 100A | FP | Siemens | 1381
MCB Isolator | 25 A | DP | ABB | 292
MCB Isolator | 32 A | DP | ABB | 292
MCB Isolator | 40 A | DP | ABB | 315
MCB Isolator | 63 A | DP | ABB | 414
MCB Isolator | 25 A | FP | ABB | 562
MCB Isolator | 32 A | FP | ABB | 562
MCB Isolator | 40 A | FP | ABB | 691
MCB Isolator | 63 A | FP | ABB | 756
MCB Isolator | 80 A | FP | ABB | 947
MCB Isolator | 100A | FP | ABB | 973
MCB Isolator | 125A | FP | ABB | 1015
MCB Isolator | 40 A | DP | L&T | 315
MCB Isolator | 63 A | DP | L&T | 402
MCB Isolator | 40 A | FP | L&T | 710
MCB Isolator | 63 A | FP | L&T | 729
MCB Isolator | 80 A | FP | L&T | 832
MCB Isolator | 100A | FP | L&T | 855
MCB Isolator | 40 A | DP | Havells | 208
MCB Isolator | 63 A | DP | Havells | 243
MCB Isolator | 40 A | FP | Havells | 676
MCB Isolator | 63 A | FP | Havells | 687
MCB Isolator | 80 A | FP | Havells | 881
MCB Isolator | 100A | FP | Havells | 881
MCB Isolator | 125A | FP | Havells | 947
MCB Isolator | 40 A | DP | Standard | 281
MCB Isolator | 63 A | DP | Standard | 360
MCB Isolator | 40 A | FP | Standard | 642
MCB Isolator | 63 A | FP | Standard | 649
MCB Isolator | 100A | FP | Standard | 862
MCB Isolator | 125A | FP | Standard | 912

## 8
Item | Way | Company | Rate | Description | GS
HTPN | 4 way | Legrand | 2851 | Supplying and fixing following double door Horizontal TPN MCB Distribution board with IP-42/43 protection, concealed in wall after cutting the wall & mending good the damages to original finish incl. Inter connection with suitable size of copper wire and neutral link & provision for earthing attachment | PWD/GS -D-9:13
HTPN | 6 way | Legrand | 3504
HTPN | 8 way | Legrand | 4194
HTPN | 4 way | Schneider | 2770
HTPN | 6 way | Schneider | 3338
HTPN | 8 way | Schneider | 3996
HTPN | 4 way | Crabtree | 2595
HTPN | 6 way | Crabtree | 3281
HTPN | 8 way | Crabtree | 4186
HTPN | 4 way | Siemens | 2492
HTPN | 6 way | Siemens | 3003
HTPN | 8 way | Siemens | 3603
HTPN | 4 way | ABB | 2292
HTPN | 6 way | ABB | 2802
HTPN | 8 way | ABB | 3356
HTPN | 4 way | L&T | 2348
HTPN | 6 way | L&T | 3002
HTPN | 8 way | L&T | 3603
HTPN | 4 way | Havells | 2419
HTPN | 6 way | Havells | 2998
HTPN | 8 way | Havells | 3832
HTPN | 4 way | Standard | 2434
HTPN | 6 way | Standard | 2842
HTPN | 8 way | Standard | 3552

## 9
Item | Conductor | Armoured | Core | Size | Company | Rate | Description | GS
Cable | Aluminium | Armoured | 2 Core | 4 sq.mm. | KEI | 169 | Supplying and Delivery following core and size of 1.1 KV Aluminium Armoured PVC/XLPE Cables | PRICE LIST : 01-01-2025
Cable | Aluminium | Armoured | 3 Core | 4 sq.mm. | KEI | 186
Cable | Aluminium | Armoured | 4 Core | 4 sq.mm. | KEI | 207
Cable | Aluminium | Armoured | 2 Core | 6 sq.mm. | KEI | 197
Cable | Aluminium | Armoured | 3 Core | 6 sq.mm. | KEI | 217
Cable | Aluminium | Armoured | 4 Core | 6 sq.mm. | KEI | 245
Cable | Aluminium | Armoured | 2 Core | 10 sq.mm. | KEI | 252
Cable | Aluminium | Armoured | 3 Core | 10 sq.mm. | KEI | 279
Cable | Aluminium | Armoured | 4 Core | 10 sq.mm. | KEI | 321
Cable | Aluminium | Armoured | 2 Core | 16 sq.mm. | KEI | 286
Cable | Aluminium | Armoured | 3 Core | 16 sq.mm. | KEI | 310
Cable | Aluminium | Armoured | 4 Core | 16 sq.mm. | KEI | 376
Cable | Aluminium | Armoured | 1 Core | 25 sq.mm. | KEI | 210
Cable | Aluminium | Armoured | 2 Core | 25 sq.mm. | KEI | 307
Cable | Aluminium | Armoured | 3 Core | 25 sq.mm. | KEI | 400
Cable | Aluminium | Armoured | 3.5 Core | 25 sq.mm. | KEI | 455
Cable | Aluminium | Armoured | 4 Core | 25 sq.mm. | KEI | 497
Cable | Aluminium | Armoured | 1 Core | 35 sq.mm. | KEI | 252
Cable | Aluminium | Armoured | 2 Core | 35 sq.mm. | KEI | 379
Cable | Aluminium | Armoured | 3 Core | 35 sq.mm. | KEI | 507
Cable | Aluminium | Armoured | 3.5 Core | 35 sq.mm. | KEI | 569
Cable | Aluminium | Armoured | 4 Core | 35 sq.mm. | KEI | 638
Cable | Aluminium | Armoured | 1 Core | 50 sq.mm. | KEI | 321
Cable | Aluminium | Armoured | 2 Core | 50 sq.mm. | KEI | 500
Cable | Aluminium | Armoured | 3 Core | 50 sq.mm. | KEI | 672
Cable | Aluminium | Armoured | 3.5 Core | 50 sq.mm. | KEI | 748
Cable | Aluminium | Armoured | 4 Core | 50 sq.mm. | KEI | 848
Cable | Aluminium | Armoured | 1 Core | 70 sq.mm. | KEI | 407
Cable | Aluminium | Armoured | 2 Core | 70 sq.mm. | KEI | 655
Cable | Aluminium | Armoured | 3 Core | 70 sq.mm. | KEI | 903
Cable | Aluminium | Armoured | 3.5 Core | 70 sq.mm. | KEI | 1010
Cable | Aluminium | Armoured | 4 Core | 70 sq.mm. | KEI | 1138
Cable | Aluminium | Armoured | 1 Core | 95 sq.mm. | KEI | 486
Cable | Aluminium | Armoured | 2 Core | 95 sq.mm. | KEI | 821
Cable | Aluminium | Armoured | 3 Core | 95 sq.mm. | KEI | 1131
Cable | Aluminium | Armoured | 3.5 Core | 95 sq.mm. | KEI | 1310
Cable | Aluminium | Armoured | 4 Core | 95 sq.mm. | KEI | 1459
Cable | Aluminium | Armoured | 1 Core | 120 sq.mm. | KEI | 579
Cable | Aluminium | Armoured | 2 Core | 120 sq.mm. | KEI | 1007
Cable | Aluminium | Armoured | 3 Core | 120 sq.mm. | KEI | 1386
Cable | Aluminium | Armoured | 3.5 Core | 120 sq.mm. | KEI | 1645
Cable | Aluminium | Armoured | 4 Core | 120 sq.mm. | KEI | 1814
Cable | Aluminium | Armoured | 1 Core | 150 sq.mm. | KEI | 690
Cable | Aluminium | Armoured | 2 Core | 150 sq.mm. | KEI | 1224
Cable | Aluminium | Armoured | 3 Core | 150 sq.mm. | KEI | 1714
Cable | Aluminium | Armoured | 3.5 Core | 150 sq.mm. | KEI | 1959
Cable | Aluminium | Armoured | 4 Core | 150 sq.mm. | KEI | 2231
Cable | Aluminium | Armoured | 1 Core | 185 sq.mm. | KEI | 834
Cable | Aluminium | Armoured | 2 Core | 185 sq.mm. | KEI | 1486
Cable | Aluminium | Armoured | 3 Core | 185 sq.mm. | KEI | 2086
Cable | Aluminium | Armoured | 3.5 Core | 185 sq.mm. | KEI | 2431
Cable | Aluminium | Armoured | 4 Core | 185 sq.mm. | KEI | 2738
Cable | Aluminium | Armoured | 1 Core | 240 sq.mm. | KEI | 1038
Cable | Aluminium | Armoured | 2 Core | 240 sq.mm. | KEI | 1869
Cable | Aluminium | Armoured | 3 Core | 240 sq.mm. | KEI | 2648
Cable | Aluminium | Armoured | 3.5 Core | 240 sq.mm. | KEI | 3059
Cable | Aluminium | Armoured | 4 Core | 240 sq.mm. | KEI | 3466
Cable | Aluminium | Armoured | 1 Core | 300 sq.mm. | KEI | 1259
Cable | Aluminium | Armoured | 2 Core | 300 sq.mm. | KEI | 2293
Cable | Aluminium | Armoured | 3 Core | 300 sq.mm. | KEI | 3252
Cable | Aluminium | Armoured | 3.5 Core | 300 sq.mm. | KEI | 3776
Cable | Aluminium | Armoured | 4 Core | 300 sq.mm. | KEI | 4276
Cable | Aluminium | Armoured | 1 Core | 400 sq.mm. | KEI | 1621
Cable | Aluminium | Armoured | 2 Core | 400 sq.mm. | KEI | 2990
Cable | Aluminium | Armoured | 3 Core | 400 sq.mm. | KEI | 4228
Cable | Aluminium | Armoured | 3.5 Core | 400 sq.mm. | KEI | 4897
Cable | Aluminium | Armoured | 4 Core | 400 sq.mm. | KEI | 5597
Cable | Aluminium | Armoured | 1 Core | 500 sq.mm. | KEI | 1966
Cable | Aluminium | Armoured | 1 Core | 630 sq.mm. | KEI | 2424
Cable | Aluminium | Armoured | 1 Core | 800 sq.mm. | KEI | 3017
Cable | Aluminium | Armoured | 1 Core | 1000 sq.mm. | KEI | 3679
Cable | Aluminium | Armoured | 1 Core | 6 sq.mm. | Gloster | 241 |  | PRICE LIST NO : GCL/LTAL/JAN-25
Cable | Aluminium | Armoured | 2 Core | 6 sq.mm. | Gloster | 263
Cable | Aluminium | Armoured | 3.5 Core | 6 sq.mm. | Gloster | 314
Cable | Aluminium | Armoured | 1 Core | 10 sq.mm. | Gloster | 305
Cable | Aluminium | Armoured | 2 Core | 10 sq.mm. | Gloster | 340
Cable | Aluminium | Armoured | 3.5 Core | 10 sq.mm. | Gloster | 432
Cable | Aluminium | Armoured | 1 Core | 16 sq.mm. | Gloster | 196
Cable | Aluminium | Armoured | 2 Core | 16 sq.mm. | Gloster | 347
Cable | Aluminium | Armoured | 3 Core | 16 sq.mm. | Gloster | 366
Cable | Aluminium | Armoured | 4 Core | 16 sq.mm. | Gloster | 462
Cable | Aluminium | Armoured | 1 Core | 25 sq.mm. | Gloster | 258
Cable | Aluminium | Armoured | 2 Core | 25 sq.mm. | Gloster | 370
Cable | Aluminium | Armoured | 3 Core | 25 sq.mm. | Gloster | 487
Cable | Aluminium | Armoured | 3.5 Core | 25 sq.mm. | Gloster | 565
Cable | Aluminium | Armoured | 4 Core | 25 sq.mm. | Gloster | 605
Cable | Aluminium | Armoured | 1 Core | 35 sq.mm. | Gloster | 312
Cable | Aluminium | Armoured | 2 Core | 35 sq.mm. | Gloster | 462
Cable | Aluminium | Armoured | 3 Core | 35 sq.mm. | Gloster | 618
Cable | Aluminium | Armoured | 3.5 Core | 35 sq.mm. | Gloster | 687
Cable | Aluminium | Armoured | 4 Core | 35 sq.mm. | Gloster | 783
Cable | Aluminium | Armoured | 1 Core | 50 sq.mm. | Gloster | 385
Cable | Aluminium | Armoured | 2 Core | 50 sq.mm. | Gloster | 598
Cable | Aluminium | Armoured | 3 Core | 50 sq.mm. | Gloster | 804
Cable | Aluminium | Armoured | 3.5 Core | 50 sq.mm. | Gloster | 930
Cable | Aluminium | Armoured | 4 Core | 50 sq.mm. | Gloster | 1046
Cable | Aluminium | Armoured | 1 Core | 70 sq.mm. | Gloster | 492
Cable | Aluminium | Armoured | 2 Core | 70 sq.mm. | Gloster | 800
Cable | Aluminium | Armoured | 3 Core | 70 sq.mm. | Gloster | 1103
Cable | Aluminium | Armoured | 3.5 Core | 70 sq.mm. | Gloster | 1253
Cable | Aluminium | Armoured | 4 Core | 70 sq.mm. | Gloster | 1421
Cable | Aluminium | Armoured | 1 Core | 95 sq.mm. | Gloster | 590
Cable | Aluminium | Armoured | 2 Core | 95 sq.mm. | Gloster | 989
Cable | Aluminium | Armoured | 3 Core | 95 sq.mm. | Gloster | 1358
Cable | Aluminium | Armoured | 3.5 Core | 95 sq.mm. | Gloster | 1565
Cable | Aluminium | Armoured | 4 Core | 95 sq.mm. | Gloster | 1772
Cable | Aluminium | Armoured | 1 Core | 120 sq.mm. | Gloster | 685
Cable | Aluminium | Armoured | 2 Core | 120 sq.mm. | Gloster | 1180
Cable | Aluminium | Armoured | 3 Core | 120 sq.mm. | Gloster | 1703
Cable | Aluminium | Armoured | 3.5 Core | 120 sq.mm. | Gloster | 1960
Cable | Aluminium | Armoured | 4 Core | 120 sq.mm. | Gloster | 2226
Cable | Aluminium | Armoured | 1 Core | 150 sq.mm. | Gloster | 816
Cable | Aluminium | Armoured | 2 Core | 150 sq.mm. | Gloster | 1451
Cable | Aluminium | Armoured | 3 Core | 150 sq.mm. | Gloster | 2091
Cable | Aluminium | Armoured | 3.5 Core | 150 sq.mm. | Gloster | 2323
Cable | Aluminium | Armoured | 4 Core | 150 sq.mm. | Gloster | 2736
Cable | Aluminium | Armoured | 1 Core | 185 sq.mm. | Gloster | 1003
Cable | Aluminium | Armoured | 2 Core | 185 sq.mm. | Gloster | 1745
Cable | Aluminium | Armoured | 3 Core | 185 sq.mm. | Gloster | 2589
Cable | Aluminium | Armoured | 3.5 Core | 185 sq.mm. | Gloster | 2941
Cable | Aluminium | Armoured | 4 Core | 185 sq.mm. | Gloster | 3366
Cable | Aluminium | Armoured | 1 Core | 240 sq.mm. | Gloster | 1239
Cable | Aluminium | Armoured | 2 Core | 240 sq.mm. | Gloster | 2313
Cable | Aluminium | Armoured | 3 Core | 240 sq.mm. | Gloster | 3306
Cable | Aluminium | Armoured | 3.5 Core | 240 sq.mm. | Gloster | 3693
Cable | Aluminium | Armoured | 4 Core | 240 sq.mm. | Gloster | 4346
Cable | Aluminium | Armoured | 1 Core | 300 sq.mm. | Gloster | 1525
Cable | Aluminium | Armoured | 2 Core | 300 sq.mm. | Gloster | 2835
Cable | Aluminium | Armoured | 3 Core | 300 sq.mm. | Gloster | 4085
Cable | Aluminium | Armoured | 3.5 Core | 300 sq.mm. | Gloster | 4544
Cable | Aluminium | Armoured | 4 Core | 300 sq.mm. | Gloster | 5357
Cable | Aluminium | Armoured | 1 Core | 400 sq.mm. | Gloster | 1926
Cable | Aluminium | Armoured | 2 Core | 400 sq.mm. | Gloster | 3681
Cable | Aluminium | Armoured | 3 Core | 400 sq.mm. | Gloster | 5222
Cable | Aluminium | Armoured | 3.5 Core | 400 sq.mm. | Gloster | 5805
Cable | Aluminium | Armoured | 4 Core | 400 sq.mm. | Gloster | 6687
Cable | Aluminium | Armoured | 1 Core | 500 sq.mm. | Gloster | 2399
Cable | Aluminium | Armoured | 2 Core | 500 sq.mm. | Gloster | 4970
Cable | Aluminium | Armoured | 3 Core | 500 sq.mm. | Gloster | 7001
Cable | Aluminium | Armoured | 3.5 Core | 500 sq.mm. | Gloster | 8205
Cable | Aluminium | Armoured | 4 Core | 500 sq.mm. | Gloster | 9245
Cable | Aluminium | Armoured | 1 Core | 630 sq.mm. | Gloster | 2961
Cable | Aluminium | Armoured | 2 Core | 630 sq.mm. | Gloster | 6114
Cable | Aluminium | Armoured | 3 Core | 630 sq.mm. | Gloster | 8899
Cable | Aluminium | Armoured | 3.5 Core | 630 sq.mm. | Gloster | 10054
Cable | Aluminium | Armoured | 4 Core | 630 sq.mm. | Gloster | 12135
Cable | Aluminium | Armoured | 1 Core | 800 sq.mm. | Gloster | 3639
Cable | Aluminium | Armoured | 1 Core | 1000 sq.mm. | Gloster | 4475
Cable | Aluminium | Armoured | 2 Core | 2.5 sq.mm. | Polycab | 175 |  | PRICE LIST DATED: 2ND JAN
Cable | Aluminium | Armoured | 3 Core | 2.5 sq.mm. | Polycab | 195
Cable | Aluminium | Armoured | 4 Core | 2.5 sq.mm. | Polycab | 217
Cable | Aluminium | Armoured | 2 Core | 4 sq.mm. | Polycab | 199
Cable | Aluminium | Armoured | 3 Core | 4 sq.mm. | Polycab | 213
Cable | Aluminium | Armoured | 4 Core | 4 sq.mm. | Polycab | 249
Cable | Aluminium | Armoured | 2 Core | 6 sq.mm. | Polycab | 241
Cable | Aluminium | Armoured | 3 Core | 6 sq.mm. | Polycab | 263
Cable | Aluminium | Armoured | 4 Core | 6 sq.mm. | Polycab | 314
Cable | Aluminium | Armoured | 2 Core | 10 sq.mm. | Polycab | 305
Cable | Aluminium | Armoured | 3 Core | 10 sq.mm. | Polycab | 340
Cable | Aluminium | Armoured | 4 Core | 10 sq.mm. | Polycab | 432
Cable | Aluminium | Armoured | 1 Core | 16 sq.mm. | Polycab | 207
Cable | Aluminium | Armoured | 2 Core | 16 sq.mm. | Polycab | 347
Cable | Aluminium | Armoured | 3 Core | 16 sq.mm. | Polycab | 366
Cable | Aluminium | Armoured | 4 Core | 16 sq.mm. | Polycab | 462
Cable | Aluminium | Armoured | 1 Core | 25 sq.mm. | Polycab | 274
Cable | Aluminium | Armoured | 2 Core | 25 sq.mm. | Polycab | 370
Cable | Aluminium | Armoured | 3 Core | 25 sq.mm. | Polycab | 487
Cable | Aluminium | Armoured | 3.5 Core | 25 sq.mm. | Polycab | 565
Cable | Aluminium | Armoured | 4 Core | 25 sq.mm. | Polycab | 605
Cable | Aluminium | Armoured | 1 Core | 35 sq.mm. | Polycab | 333
Cable | Aluminium | Armoured | 2 Core | 35 sq.mm. | Polycab | 462
Cable | Aluminium | Armoured | 3 Core | 35 sq.mm. | Polycab | 618
Cable | Aluminium | Armoured | 3.5 Core | 35 sq.mm. | Polycab | 687
Cable | Aluminium | Armoured | 4 Core | 35 sq.mm. | Polycab | 783
Cable | Aluminium | Armoured | 1 Core | 50 sq.mm. | Polycab | 410
Cable | Aluminium | Armoured | 2 Core | 50 sq.mm. | Polycab | 598
Cable | Aluminium | Armoured | 3 Core | 50 sq.mm. | Polycab | 804
Cable | Aluminium | Armoured | 3.5 Core | 50 sq.mm. | Polycab | 930
Cable | Aluminium | Armoured | 4 Core | 50 sq.mm. | Polycab | 1046
Cable | Aluminium | Armoured | 1 Core | 70 sq.mm. | Polycab | 528
Cable | Aluminium | Armoured | 2 Core | 70 sq.mm. | Polycab | 800
Cable | Aluminium | Armoured | 3 Core | 70 sq.mm. | Polycab | 1103
Cable | Aluminium | Armoured | 3.5 Core | 70 sq.mm. | Polycab | 1253
Cable | Aluminium | Armoured | 4 Core | 70 sq.mm. | Polycab | 1421
Cable | Aluminium | Armoured | 1 Core | 95 sq.mm. | Polycab | 577
Cable | Aluminium | Armoured | 2 Core | 95 sq.mm. | Polycab | 989
Cable | Aluminium | Armoured | 3 Core | 95 sq.mm. | Polycab | 1358
Cable | Aluminium | Armoured | 3.5 Core | 95 sq.mm. | Polycab | 1565
Cable | Aluminium | Armoured | 4 Core | 95 sq.mm. | Polycab | 1772
Cable | Aluminium | Armoured | 1 Core | 120 sq.mm. | Polycab | 715
Cable | Aluminium | Armoured | 2 Core | 120 sq.mm. | Polycab | 1180
Cable | Aluminium | Armoured | 3 Core | 120 sq.mm. | Polycab | 1703
Cable | Aluminium | Armoured | 3.5 Core | 120 sq.mm. | Polycab | 1960
Cable | Aluminium | Armoured | 4 Core | 120 sq.mm. | Polycab | 2226
Cable | Aluminium | Armoured | 1 Core | 150 sq.mm. | Polycab | 853
Cable | Aluminium | Armoured | 2 Core | 150 sq.mm. | Polycab | 1451
Cable | Aluminium | Armoured | 3 Core | 150 sq.mm. | Polycab | 2091
Cable | Aluminium | Armoured | 3.5 Core | 150 sq.mm. | Polycab | 2323
Cable | Aluminium | Armoured | 4 Core | 150 sq.mm. | Polycab | 2736
Cable | Aluminium | Armoured | 1 Core | 185 sq.mm. | Polycab | 1003
Cable | Aluminium | Armoured | 2 Core | 185 sq.mm. | Polycab | 1745
Cable | Aluminium | Armoured | 3 Core | 185 sq.mm. | Polycab | 2589
Cable | Aluminium | Armoured | 3.5 Core | 185 sq.mm. | Polycab | 2941
Cable | Aluminium | Armoured | 4 Core | 185 sq.mm. | Polycab | 3366
Cable | Aluminium | Armoured | 1 Core | 240 sq.mm. | Polycab | 1239
Cable | Aluminium | Armoured | 2 Core | 240 sq.mm. | Polycab | 2313
Cable | Aluminium | Armoured | 3 Core | 240 sq.mm. | Polycab | 3306
Cable | Aluminium | Armoured | 3.5 Core | 240 sq.mm. | Polycab | 3693
Cable | Aluminium | Armoured | 4 Core | 240 sq.mm. | Polycab | 4346
Cable | Aluminium | Armoured | 1 Core | 300 sq.mm. | Polycab | 1525
Cable | Aluminium | Armoured | 2 Core | 300 sq.mm. | Polycab | 2835
Cable | Aluminium | Armoured | 3 Core | 300 sq.mm. | Polycab | 4085
Cable | Aluminium | Armoured | 3.5 Core | 300 sq.mm. | Polycab | 4544
Cable | Aluminium | Armoured | 4 Core | 300 sq.mm. | Polycab | 5357
Cable | Aluminium | Armoured | 1 Core | 400 sq.mm. | Polycab | 1926
Cable | Aluminium | Armoured | 2 Core | 400 sq.mm. | Polycab | 3681
Cable | Aluminium | Armoured | 3 Core | 400 sq.mm. | Polycab | 5222
Cable | Aluminium | Armoured | 3.5 Core | 400 sq.mm. | Polycab | 5805
Cable | Aluminium | Armoured | 4 Core | 400 sq.mm. | Polycab | 6687
Cable | Aluminium | Armoured | 1 Core | 500 sq.mm. | Polycab | 2399
Cable | Aluminium | Armoured | 2 Core | 500 sq.mm. | Polycab | 4970
Cable | Aluminium | Armoured | 3 Core | 500 sq.mm. | Polycab | 7001
Cable | Aluminium | Armoured | 3.5 Core | 500 sq.mm. | Polycab | 8205
Cable | Aluminium | Armoured | 4 Core | 500 sq.mm. | Polycab | 9245
Cable | Aluminium | Armoured | 1 Core | 630 sq.mm. | Polycab | 2961
Cable | Aluminium | Armoured | 2 Core | 630 sq.mm. | Polycab | 6114
Cable | Aluminium | Armoured | 3 Core | 630 sq.mm. | Polycab | 8899
Cable | Aluminium | Armoured | 3.5 Core | 630 sq.mm. | Polycab | 10054
Cable | Aluminium | Armoured | 4 Core | 630 sq.mm. | Polycab | 12135
Cable | Aluminium | Un-Armoured | 2 Core | 4 sq.mm. | KEI | 86 | Supplying and Delivery following core and size of 1.1 KV Aluminium Un-Armoured PVC/XLPE Cables | PRICE LIST : 01-01-2025
Cable | Aluminium | Un-Armoured | 3 Core | 4 sq.mm. | KEI | 100
Cable | Aluminium | Un-Armoured | 4 Core | 4 sq.mm. | KEI | 114
Cable | Aluminium | Un-Armoured | 2 Core | 6 sq.mm. | KEI | 103
Cable | Aluminium | Un-Armoured | 3 Core | 6 sq.mm. | KEI | 124
Cable | Aluminium | Un-Armoured | 4 Core | 6 sq.mm. | KEI | 145
Cable | Aluminium | Un-Armoured | 2 Core | 10 sq.mm. | KEI | 145
Cable | Aluminium | Un-Armoured | 3 Core | 10 sq.mm. | KEI | 176
Cable | Aluminium | Un-Armoured | 4 Core | 10 sq.mm. | KEI | 207
Cable | Aluminium | Un-Armoured | 2 Core | 16 sq.mm. | KEI | 183
Cable | Aluminium | Un-Armoured | 3 Core | 16 sq.mm. | KEI | 231
Cable | Aluminium | Un-Armoured | 4 Core | 16 sq.mm. | KEI | 290
Cable | Aluminium | Un-Armoured | 1 Core | 25 sq.mm. | KEI | 117
Cable | Aluminium | Un-Armoured | 2 Core | 25 sq.mm. | KEI | 241
Cable | Aluminium | Un-Armoured | 3 Core | 25 sq.mm. | KEI | 324
Cable | Aluminium | Un-Armoured | 3.5 Core | 25 sq.mm. | KEI | 379
Cable | Aluminium | Un-Armoured | 4 Core | 25 sq.mm. | KEI | 414
Cable | Aluminium | Un-Armoured | 1 Core | 35 sq.mm. | KEI | 148
Cable | Aluminium | Un-Armoured | 2 Core | 35 sq.mm. | KEI | 307
Cable | Aluminium | Un-Armoured | 3 Core | 35 sq.mm. | KEI | 428
Cable | Aluminium | Un-Armoured | 3.5 Core | 35 sq.mm. | KEI | 479
Cable | Aluminium | Un-Armoured | 4 Core | 35 sq.mm. | KEI | 545
Cable | Aluminium | Un-Armoured | 1 Core | 50 sq.mm. | KEI | 203
Cable | Aluminium | Un-Armoured | 2 Core | 50 sq.mm. | KEI | 417
Cable | Aluminium | Un-Armoured | 3 Core | 50 sq.mm. | KEI | 579
Cable | Aluminium | Un-Armoured | 3.5 Core | 50 sq.mm. | KEI | 659
Cable | Aluminium | Un-Armoured | 4 Core | 50 sq.mm. | KEI | 752
Cable | Aluminium | Un-Armoured | 1 Core | 70 sq.mm. | KEI | 272
Cable | Aluminium | Un-Armoured | 2 Core | 70 sq.mm. | KEI | 559
Cable | Aluminium | Un-Armoured | 3 Core | 70 sq.mm. | KEI | 797
Cable | Aluminium | Un-Armoured | 3.5 Core | 70 sq.mm. | KEI | 907
Cable | Aluminium | Un-Armoured | 4 Core | 70 sq.mm. | KEI | 1024
Cable | Aluminium | Un-Armoured | 1 Core | 95 sq.mm. | KEI | 348
Cable | Aluminium | Un-Armoured | 2 Core | 95 sq.mm. | KEI | 721
Cable | Aluminium | Un-Armoured | 3 Core | 95 sq.mm. | KEI | 1017
Cable | Aluminium | Un-Armoured | 3.5 Core | 95 sq.mm. | KEI | 1193
Cable | Aluminium | Un-Armoured | 4 Core | 95 sq.mm. | KEI | 1338
Cable | Aluminium | Un-Armoured | 1 Core | 120 sq.mm. | KEI | 431
Cable | Aluminium | Un-Armoured | 2 Core | 120 sq.mm. | KEI | 897
Cable | Aluminium | Un-Armoured | 3 Core | 120 sq.mm. | KEI | 1269
Cable | Aluminium | Un-Armoured | 3.5 Core | 120 sq.mm. | KEI | 1507
Cable | Aluminium | Un-Armoured | 4 Core | 120 sq.mm. | KEI | 1690
Cable | Aluminium | Un-Armoured | 1 Core | 150 sq.mm. | KEI | 541
Cable | Aluminium | Un-Armoured | 2 Core | 150 sq.mm. | KEI | 1117
Cable | Aluminium | Un-Armoured | 3 Core | 150 sq.mm. | KEI | 1597
Cable | Aluminium | Un-Armoured | 3.5 Core | 150 sq.mm. | KEI | 1821
Cable | Aluminium | Un-Armoured | 4 Core | 150 sq.mm. | KEI | 2103
Cable | Aluminium | Un-Armoured | 1 Core | 185 sq.mm. | KEI | 659
Cable | Aluminium | Un-Armoured | 2 Core | 185 sq.mm. | KEI | 1359
Cable | Aluminium | Un-Armoured | 3 Core | 185 sq.mm. | KEI | 1941
Cable | Aluminium | Un-Armoured | 3.5 Core | 185 sq.mm. | KEI | 2279
Cable | Aluminium | Un-Armoured | 4 Core | 185 sq.mm. | KEI | 2583
Cable | Aluminium | Un-Armoured | 1 Core | 240 sq.mm. | KEI | 838
Cable | Aluminium | Un-Armoured | 2 Core | 240 sq.mm. | KEI | 1731
Cable | Aluminium | Un-Armoured | 3 Core | 240 sq.mm. | KEI | 2497
Cable | Aluminium | Un-Armoured | 3.5 Core | 240 sq.mm. | KEI | 2897
Cable | Aluminium | Un-Armoured | 4 Core | 240 sq.mm. | KEI | 3303
Cable | Aluminium | Un-Armoured | 1 Core | 300 sq.mm. | KEI | 1034
Cable | Aluminium | Un-Armoured | 2 Core | 300 sq.mm. | KEI | 2138
Cable | Aluminium | Un-Armoured | 3 Core | 300 sq.mm. | KEI | 3086
Cable | Aluminium | Un-Armoured | 3.5 Core | 300 sq.mm. | KEI | 3590
Cable | Aluminium | Un-Armoured | 4 Core | 300 sq.mm. | KEI | 4107
Cable | Aluminium | Un-Armoured | 1 Core | 400 sq.mm. | KEI | 1369
Cable | Aluminium | Un-Armoured | 2 Core | 400 sq.mm. | KEI | 2814
Cable | Aluminium | Un-Armoured | 3 Core | 400 sq.mm. | KEI | 4055
Cable | Aluminium | Un-Armoured | 3.5 Core | 400 sq.mm. | KEI | 4721
Cable | Aluminium | Un-Armoured | 4 Core | 400 sq.mm. | KEI | 5400
Cable | Aluminium | Un-Armoured | 1 Core | 500 sq.mm. | KEI | 1690
Cable | Aluminium | Un-Armoured | 1 Core | 630 sq.mm. | KEI | 2121
Cable | Aluminium | Un-Armoured | 1 Core | 800 sq.mm. | KEI | 2672
Cable | Aluminium | Un-Armoured | 1 Core | 1000 sq.mm. | KEI | 3341
Cable | Aluminium | Un-Armoured | 2 Core | 6 sq.mm. | Gloster | 155 |  | PRICE LIST NO : GCL/LTAL/JAN-25
Cable | Aluminium | Un-Armoured | 3 Core | 6 sq.mm. | Gloster | 184
Cable | Aluminium | Un-Armoured | 4 Core | 6 sq.mm. | Gloster | 225
Cable | Aluminium | Un-Armoured | 2 Core | 10 sq.mm. | Gloster | 225
Cable | Aluminium | Un-Armoured | 3 Core | 10 sq.mm. | Gloster | 250
Cable | Aluminium | Un-Armoured | 4 Core | 10 sq.mm. | Gloster | 295
Cable | Aluminium | Un-Armoured | 1 Core | 16 sq.mm. | Gloster | 109
Cable | Aluminium | Un-Armoured | 2 Core | 16 sq.mm. | Gloster | 228
Cable | Aluminium | Un-Armoured | 3 Core | 16 sq.mm. | Gloster | 283
Cable | Aluminium | Un-Armoured | 4 Core | 16 sq.mm. | Gloster | 374
Cable | Aluminium | Un-Armoured | 1 Core | 25 sq.mm. | Gloster | 157
Cable | Aluminium | Un-Armoured | 2 Core | 25 sq.mm. | Gloster | 295
Cable | Aluminium | Un-Armoured | 3 Core | 25 sq.mm. | Gloster | 415
Cable | Aluminium | Un-Armoured | 3.5 Core | 25 sq.mm. | Gloster | 526
Cable | Aluminium | Un-Armoured | 4 Core | 25 sq.mm. | Gloster | 553
Cable | Aluminium | Un-Armoured | 1 Core | 35 sq.mm. | Gloster | 203
Cable | Aluminium | Un-Armoured | 2 Core | 35 sq.mm. | Gloster | 387
Cable | Aluminium | Un-Armoured | 3 Core | 35 sq.mm. | Gloster | 549
Cable | Aluminium | Un-Armoured | 3.5 Core | 35 sq.mm. | Gloster | 594
Cable | Aluminium | Un-Armoured | 4 Core | 35 sq.mm. | Gloster | 659
Cable | Aluminium | Un-Armoured | 1 Core | 50 sq.mm. | Gloster | 261
Cable | Aluminium | Un-Armoured | 2 Core | 50 sq.mm. | Gloster | 486
Cable | Aluminium | Un-Armoured | 3 Core | 50 sq.mm. | Gloster | 676
Cable | Aluminium | Un-Armoured | 3.5 Core | 50 sq.mm. | Gloster | 805
Cable | Aluminium | Un-Armoured | 4 Core | 50 sq.mm. | Gloster | 882
Cable | Aluminium | Un-Armoured | 1 Core | 70 sq.mm. | Gloster | 360
Cable | Aluminium | Un-Armoured | 2 Core | 70 sq.mm. | Gloster | 699
Cable | Aluminium | Un-Armoured | 3 Core | 70 sq.mm. | Gloster | 973
Cable | Aluminium | Un-Armoured | 3.5 Core | 70 sq.mm. | Gloster | 1100
Cable | Aluminium | Un-Armoured | 4 Core | 70 sq.mm. | Gloster | 1266
Cable | Aluminium | Un-Armoured | 1 Core | 95 sq.mm. | Gloster | 463
Cable | Aluminium | Un-Armoured | 2 Core | 95 sq.mm. | Gloster | 829
Cable | Aluminium | Un-Armoured | 3 Core | 95 sq.mm. | Gloster | 1184
Cable | Aluminium | Un-Armoured | 3.5 Core | 95 sq.mm. | Gloster | 1400
Cable | Aluminium | Un-Armoured | 4 Core | 95 sq.mm. | Gloster | 1509
Cable | Aluminium | Un-Armoured | 1 Core | 120 sq.mm. | Gloster | 577
Cable | Aluminium | Un-Armoured | 2 Core | 120 sq.mm. | Gloster | 1033
Cable | Aluminium | Un-Armoured | 3 Core | 120 sq.mm. | Gloster | 1592
Cable | Aluminium | Un-Armoured | 3.5 Core | 120 sq.mm. | Gloster | 1800
Cable | Aluminium | Un-Armoured | 4 Core | 120 sq.mm. | Gloster | 1924
Cable | Aluminium | Un-Armoured | 1 Core | 150 sq.mm. | Gloster | 713
Cable | Aluminium | Un-Armoured | 2 Core | 150 sq.mm. | Gloster | 1285
Cable | Aluminium | Un-Armoured | 3 Core | 150 sq.mm. | Gloster | 1873
Cable | Aluminium | Un-Armoured | 3.5 Core | 150 sq.mm. | Gloster | 2106
Cable | Aluminium | Un-Armoured | 4 Core | 150 sq.mm. | Gloster | 2382
Cable | Aluminium | Un-Armoured | 1 Core | 185 sq.mm. | Gloster | 883
Cable | Aluminium | Un-Armoured | 2 Core | 185 sq.mm. | Gloster | 1532
Cable | Aluminium | Un-Armoured | 3 Core | 185 sq.mm. | Gloster | 2361
Cable | Aluminium | Un-Armoured | 3.5 Core | 185 sq.mm. | Gloster | 2693
Cable | Aluminium | Un-Armoured | 4 Core | 185 sq.mm. | Gloster | 2949
Cable | Aluminium | Un-Armoured | 1 Core | 240 sq.mm. | Gloster | 1120
Cable | Aluminium | Un-Armoured | 2 Core | 240 sq.mm. | Gloster | 2004
Cable | Aluminium | Un-Armoured | 3 Core | 240 sq.mm. | Gloster | 3047
Cable | Aluminium | Un-Armoured | 3.5 Core | 240 sq.mm. | Gloster | 3296
Cable | Aluminium | Un-Armoured | 4 Core | 240 sq.mm. | Gloster | 3852
Cable | Aluminium | Un-Armoured | 1 Core | 300 sq.mm. | Gloster | 1385
Cable | Aluminium | Un-Armoured | 2 Core | 300 sq.mm. | Gloster | 2449
Cable | Aluminium | Un-Armoured | 3 Core | 300 sq.mm. | Gloster | 3735
Cable | Aluminium | Un-Armoured | 3.5 Core | 300 sq.mm. | Gloster | 4271
Cable | Aluminium | Un-Armoured | 4 Core | 300 sq.mm. | Gloster | 4692
Cable | Aluminium | Un-Armoured | 1 Core | 400 sq.mm. | Gloster | 1782
Cable | Aluminium | Un-Armoured | 2 Core | 400 sq.mm. | Gloster | 3056
Cable | Aluminium | Un-Armoured | 3 Core | 400 sq.mm. | Gloster | 4660
Cable | Aluminium | Un-Armoured | 3.5 Core | 400 sq.mm. | Gloster | 5337
Cable | Aluminium | Un-Armoured | 4 Core | 400 sq.mm. | Gloster | 5997
Cable | Aluminium | Un-Armoured | 1 Core | 500 sq.mm. | Gloster | 2240
Cable | Aluminium | Un-Armoured | 2 Core | 500 sq.mm. | Gloster | 3898
Cable | Aluminium | Un-Armoured | 3 Core | 500 sq.mm. | Gloster | 6596
Cable | Aluminium | Un-Armoured | 3.5 Core | 500 sq.mm. | Gloster | 7365
Cable | Aluminium | Un-Armoured | 4 Core | 500 sq.mm. | Gloster | 8365
Cable | Aluminium | Un-Armoured | 1 Core | 630 sq.mm. | Gloster | 2774
Cable | Aluminium | Un-Armoured | 2 Core | 630 sq.mm. | Gloster | 4963
Cable | Aluminium | Un-Armoured | 3 Core | 630 sq.mm. | Gloster | 8274
Cable | Aluminium | Un-Armoured | 3.5 Core | 630 sq.mm. | Gloster | 9770
Cable | Aluminium | Un-Armoured | 4 Core | 630 sq.mm. | Gloster | 11193
Cable | Aluminium | Un-Armoured | 1 Core | 800 sq.mm. | Gloster | 3463
Cable | Aluminium | Un-Armoured | 1 Core | 1000 sq.mm. | Gloster | 4366
Cable | Copper | Un-Armoured | 2 Core | 4 sq.mm. | KEI | 300 | Supplying and Delivery following core and size of 1.1 KV Copper Un-Armoured PVC/XLPE Cables | PRICE LIST : 01-01-2025
Cable | Copper | Un-Armoured | 3 Core | 4 sq.mm. | KEI | 414
Cable | Copper | Un-Armoured | 4 Core | 4 sq.mm. | KEI | 538
Cable | Copper | Un-Armoured | 2 Core | 6 sq.mm. | KEI | 431
Cable | Copper | Un-Armoured | 3 Core | 6 sq.mm. | KEI | 597
Cable | Copper | Un-Armoured | 4 Core | 6 sq.mm. | KEI | 783
Cable | Copper | Un-Armoured | 2 Core | 10 sq.mm. | KEI | 690
Cable | Copper | Un-Armoured | 3 Core | 10 sq.mm. | KEI | 966
Cable | Copper | Un-Armoured | 4 Core | 10 sq.mm. | KEI | 1272
Cable | Copper | Un-Armoured | 1 Core | 16 sq.mm. | KEI | 521
Cable | Copper | Un-Armoured | 2 Core | 16 sq.mm. | KEI | 1055
Cable | Copper | Un-Armoured | 3 Core | 16 sq.mm. | KEI | 1466
Cable | Copper | Un-Armoured | 4 Core | 16 sq.mm. | KEI | 1952
Cable | Copper | Un-Armoured | 1 Core | 25 sq.mm. | KEI | 831
Cable | Copper | Un-Armoured | 2 Core | 25 sq.mm. | KEI | 1603
Cable | Copper | Un-Armoured | 3 Core | 25 sq.mm. | KEI | 2376
Cable | Copper | Un-Armoured | 3.5 Core | 25 sq.mm. | KEI | 2879
Cable | Copper | Un-Armoured | 4 Core | 25 sq.mm. | KEI | 3162
Cable | Copper | Un-Armoured | 1 Core | 35 sq.mm. | KEI | 1152
Cable | Copper | Un-Armoured | 2 Core | 35 sq.mm. | KEI | 2217
Cable | Copper | Un-Armoured | 3 Core | 35 sq.mm. | KEI | 3303
Cable | Copper | Un-Armoured | 3.5 Core | 35 sq.mm. | KEI | 3803
Cable | Copper | Un-Armoured | 4 Core | 35 sq.mm. | KEI | 4390
Cable | Copper | Un-Armoured | 1 Core | 50 sq.mm. | KEI | 1631
Cable | Copper | Un-Armoured | 2 Core | 50 sq.mm. | KEI | 3145
Cable | Copper | Un-Armoured | 3 Core | 50 sq.mm. | KEI | 4686
Cable | Copper | Un-Armoured | 3.5 Core | 50 sq.mm. | KEI | 5466
Cable | Copper | Un-Armoured | 4 Core | 50 sq.mm. | KEI | 6245
Cable | Copper | Un-Armoured | 1 Core | 70 sq.mm. | KEI | 2272
Cable | Copper | Un-Armoured | 2 Core | 70 sq.mm. | KEI | 4379
Cable | Copper | Un-Armoured | 3 Core | 70 sq.mm. | KEI | 6545
Cable | Copper | Un-Armoured | 3.5 Core | 70 sq.mm. | KEI | 7631
Cable | Copper | Un-Armoured | 4 Core | 70 sq.mm. | KEI | 8717
Cable | Copper | Un-Armoured | 1 Core | 95 sq.mm. | KEI | 2948
Cable | Copper | Un-Armoured | 2 Core | 95 sq.mm. | KEI | 5924
Cable | Copper | Un-Armoured | 3 Core | 95 sq.mm. | KEI | 8841
Cable | Copper | Un-Armoured | 3.5 Core | 95 sq.mm. | KEI | 10400
Cable | Copper | Un-Armoured | 4 Core | 95 sq.mm. | KEI | 11793
Cable | Copper | Un-Armoured | 1 Core | 120 sq.mm. | KEI | 3714
Cable | Copper | Un-Armoured | 2 Core | 120 sq.mm. | KEI | 7466
Cable | Copper | Un-Armoured | 3 Core | 120 sq.mm. | KEI | 11152
Cable | Copper | Un-Armoured | 3.5 Core | 120 sq.mm. | KEI | 13317
Cable | Copper | Un-Armoured | 4 Core | 120 sq.mm. | KEI | 14869
Cable | Copper | Un-Armoured | 1 Core | 150 sq.mm. | KEI | 4645
Cable | Copper | Un-Armoured | 2 Core | 150 sq.mm. | KEI | 9338
Cable | Copper | Un-Armoured | 3 Core | 150 sq.mm. | KEI | 13952
Cable | Copper | Un-Armoured | 3.5 Core | 150 sq.mm. | KEI | 16103
Cable | Copper | Un-Armoured | 4 Core | 150 sq.mm. | KEI | 18583
Cable | Copper | Un-Armoured | 1 Core | 185 sq.mm. | KEI | 5721
Cable | Copper | Un-Armoured | 2 Core | 185 sq.mm. | KEI | 11490
Cable | Copper | Un-Armoured | 3 Core | 185 sq.mm. | KEI | 17183
Cable | Copper | Un-Armoured | 3.5 Core | 185 sq.mm. | KEI | 20128
Cable | Copper | Un-Armoured | 4 Core | 185 sq.mm. | KEI | 22910
Cable | Copper | Un-Armoured | 1 Core | 240 sq.mm. | KEI | 7403
Cable | Copper | Un-Armoured | 2 Core | 240 sq.mm. | KEI | 14886
Cable | Copper | Un-Armoured | 3 Core | 240 sq.mm. | KEI | 22262
Cable | Copper | Un-Armoured | 3.5 Core | 240 sq.mm. | KEI | 25966
Cable | Copper | Un-Armoured | 4 Core | 240 sq.mm. | KEI | 29672
Cable | Copper | Un-Armoured | 1 Core | 300 sq.mm. | KEI | 9241
Cable | Copper | Un-Armoured | 2 Core | 300 sq.mm. | KEI | 18583
Cable | Copper | Un-Armoured | 3 Core | 300 sq.mm. | KEI | 27797
Cable | Copper | Un-Armoured | 3.5 Core | 300 sq.mm. | KEI | 32441
Cable | Copper | Un-Armoured | 4 Core | 300 sq.mm. | KEI | 37079
Cable | Copper | Un-Armoured | 1 Core | 400 sq.mm. | KEI | 12314
Cable | Copper | Un-Armoured | 2 Core | 400 sq.mm. | KEI | 24724
Cable | Copper | Un-Armoured | 3 Core | 400 sq.mm. | KEI | 37010
Cable | Copper | Un-Armoured | 3.5 Core | 400 sq.mm. | KEI | 42776
Cable | Copper | Un-Armoured | 4 Core | 400 sq.mm. | KEI | 49662
Cable | Copper | Un-Armoured | 1 Core | 500 sq.mm. | KEI | 15376
Cable | Copper | Un-Armoured | 1 Core | 630 sq.mm. | KEI | 19369
Cable | Copper | Un-Armoured | 1 Core | 800 sq.mm. | KEI | 24576
Cable | Copper | Un-Armoured | 1 Core | 1000 sq.mm. | KEI | 30707
Cable | Copper | Un-Armoured | 2 Core | 4 sq.mm. | Gloster | 344 |  | PRICE LIST NO : GCL/LTCuP/JAN-25
Cable | Copper | Un-Armoured | 3 Core | 4 sq.mm. | Gloster | 490
Cable | Copper | Un-Armoured | 4 Core | 4 sq.mm. | Gloster | 606
Cable | Copper | Un-Armoured | 2 Core | 6 sq.mm. | Gloster | 502
Cable | Copper | Un-Armoured | 3 Core | 6 sq.mm. | Gloster | 723
Cable | Copper | Un-Armoured | 4 Core | 6 sq.mm. | Gloster | 891
Cable | Copper | Un-Armoured | 2 Core | 10 sq.mm. | Gloster | 871
Cable | Copper | Un-Armoured | 3 Core | 10 sq.mm. | Gloster | 1227
Cable | Copper | Un-Armoured | 4 Core | 10 sq.mm. | Gloster | 1428
Cable | Copper | Un-Armoured | 1 Core | 16 sq.mm. | Gloster | 645
Cable | Copper | Un-Armoured | 2 Core | 16 sq.mm. | Gloster | 1228
Cable | Copper | Un-Armoured | 3 Core | 16 sq.mm. | Gloster | 1781
Cable | Copper | Un-Armoured | 4 Core | 16 sq.mm. | Gloster | 2235
Cable | Copper | Un-Armoured | 1 Core | 25 sq.mm. | Gloster | 1023
Cable | Copper | Un-Armoured | 2 Core | 25 sq.mm. | Gloster | 2019
Cable | Copper | Un-Armoured | 3 Core | 25 sq.mm. | Gloster | 2807
Cable | Copper | Un-Armoured | 3.5 Core | 25 sq.mm. | Gloster | 3344
Cable | Copper | Un-Armoured | 4 Core | 25 sq.mm. | Gloster | 3675
Cable | Copper | Un-Armoured | 1 Core | 35 sq.mm. | Gloster | 1415
Cable | Copper | Un-Armoured | 2 Core | 35 sq.mm. | Gloster | 2797
Cable | Copper | Un-Armoured | 3 Core | 35 sq.mm. | Gloster | 3910
Cable | Copper | Un-Armoured | 3.5 Core | 35 sq.mm. | Gloster | 4502
Cable | Copper | Un-Armoured | 4 Core | 35 sq.mm. | Gloster | 5266
Cable | Copper | Un-Armoured | 1 Core | 50 sq.mm. | Gloster | 1937
Cable | Copper | Un-Armoured | 2 Core | 50 sq.mm. | Gloster | 3835
Cable | Copper | Un-Armoured | 3 Core | 50 sq.mm. | Gloster | 5316
Cable | Copper | Un-Armoured | 3.5 Core | 50 sq.mm. | Gloster | 6368
Cable | Copper | Un-Armoured | 4 Core | 50 sq.mm. | Gloster | 7040
Cable | Copper | Un-Armoured | 1 Core | 70 sq.mm. | Gloster | 2759
Cable | Copper | Un-Armoured | 2 Core | 70 sq.mm. | Gloster | 5469
Cable | Copper | Un-Armoured | 3 Core | 70 sq.mm. | Gloster | 7830
Cable | Copper | Un-Armoured | 3.5 Core | 70 sq.mm. | Gloster | 9186
Cable | Copper | Un-Armoured | 4 Core | 70 sq.mm. | Gloster | 10401
Cable | Copper | Un-Armoured | 1 Core | 95 sq.mm. | Gloster | 3761
Cable | Copper | Un-Armoured | 2 Core | 95 sq.mm. | Gloster | 7475
Cable | Copper | Un-Armoured | 3 Core | 95 sq.mm. | Gloster | 11204
Cable | Copper | Un-Armoured | 3.5 Core | 95 sq.mm. | Gloster | 13039
Cable | Copper | Un-Armoured | 4 Core | 95 sq.mm. | Gloster | 14586
Cable | Copper | Un-Armoured | 1 Core | 120 sq.mm. | Gloster | 4741
Cable | Copper | Un-Armoured | 2 Core | 120 sq.mm. | Gloster | 9448
Cable | Copper | Un-Armoured | 3 Core | 120 sq.mm. | Gloster | 13115
Cable | Copper | Un-Armoured | 3.5 Core | 120 sq.mm. | Gloster | 16674
Cable | Copper | Un-Armoured | 4 Core | 120 sq.mm. | Gloster | 18674
Cable | Copper | Un-Armoured | 1 Core | 150 sq.mm. | Gloster | 5924
Cable | Copper | Un-Armoured | 2 Core | 150 sq.mm. | Gloster | 11783
Cable | Copper | Un-Armoured | 3 Core | 150 sq.mm. | Gloster | 17563
Cable | Copper | Un-Armoured | 3.5 Core | 150 sq.mm. | Gloster | 20286
Cable | Copper | Un-Armoured | 4 Core | 150 sq.mm. | Gloster | 23343
Cable | Copper | Un-Armoured | 1 Core | 185 sq.mm. | Gloster | 7270
Cable | Copper | Un-Armoured | 2 Core | 185 sq.mm. | Gloster | 14233
Cable | Copper | Un-Armoured | 3 Core | 185 sq.mm. | Gloster | 21675
Cable | Copper | Un-Armoured | 3.5 Core | 185 sq.mm. | Gloster | 25343
Cable | Copper | Un-Armoured | 4 Core | 185 sq.mm. | Gloster | 28900
Cable | Copper | Un-Armoured | 1 Core | 240 sq.mm. | Gloster | 9392
Cable | Copper | Un-Armoured | 2 Core | 240 sq.mm. | Gloster | 18224
Cable | Copper | Un-Armoured | 3 Core | 240 sq.mm. | Gloster | 28328
Cable | Copper | Un-Armoured | 3.5 Core | 240 sq.mm. | Gloster | 33092
Cable | Copper | Un-Armoured | 4 Core | 240 sq.mm. | Gloster | 38294
Cable | Copper | Un-Armoured | 1 Core | 300 sq.mm. | Gloster | 11716
Cable | Copper | Un-Armoured | 2 Core | 300 sq.mm. | Gloster | 22708
Cable | Copper | Un-Armoured | 3 Core | 300 sq.mm. | Gloster | 35133
Cable | Copper | Un-Armoured | 3.5 Core | 300 sq.mm. | Gloster | 40800
Cable | Copper | Un-Armoured | 4 Core | 300 sq.mm. | Gloster | 47290
Cable | Copper | Un-Armoured | 1 Core | 400 sq.mm. | Gloster | 15395
Cable | Copper | Un-Armoured | 2 Core | 400 sq.mm. | Gloster | 30308
Cable | Copper | Un-Armoured | 3 Core | 400 sq.mm. | Gloster | 43796
Cable | Copper | Un-Armoured | 3.5 Core | 400 sq.mm. | Gloster | 49885
Cable | Copper | Un-Armoured | 4 Core | 400 sq.mm. | Gloster | 62217
Cable | Copper | Un-Armoured | 1 Core | 500 sq.mm. | Gloster | 19452
Cable | Copper | Un-Armoured | 1 Core | 630 sq.mm. | Gloster | 24454
Cable | Copper | Un-Armoured | 1 Core | 800 sq.mm. | Gloster | 31123
Cable | Copper | Un-Armoured | 1 Core | 1000 sq.mm. | Gloster | 38905
Cable | Copper | Armoured | 2 Core | 4 sq.mm. | KEI | 372 | Supplying and Delivery following core and size of 1.1 KV Copper Armoured PVC/XLPE Cables | PRICE LIST : 01-01-2025
Cable | Copper | Armoured | 3 Core | 4 sq.mm. | KEI | 479
Cable | Copper | Armoured | 4 Core | 4 sq.mm. | KEI | 607
Cable | Copper | Armoured | 2 Core | 6 sq.mm. | KEI | 503
Cable | Copper | Armoured | 3 Core | 6 sq.mm. | KEI | 662
Cable | Copper | Armoured | 4 Core | 6 sq.mm. | KEI | 848
Cable | Copper | Armoured | 2 Core | 10 sq.mm. | KEI | 762
Cable | Copper | Armoured | 3 Core | 10 sq.mm. | KEI | 1028
Cable | Copper | Armoured | 4 Core | 10 sq.mm. | KEI | 1334
Cable | Copper | Armoured | 1 Core | 16 sq.mm. | KEI | 583
Cable | Copper | Armoured | 2 Core | 16 sq.mm. | KEI | 1110
Cable | Copper | Armoured | 3 Core | 16 sq.mm. | KEI | 1514
Cable | Copper | Armoured | 4 Core | 16 sq.mm. | KEI | 2000
Cable | Copper | Armoured | 1 Core | 25 sq.mm. | KEI | 890
Cable | Copper | Armoured | 2 Core | 25 sq.mm. | KEI | 1672
Cable | Copper | Armoured | 3 Core | 25 sq.mm. | KEI | 2462
Cable | Copper | Armoured | 3.5 Core | 25 sq.mm. | KEI | 2972
Cable | Copper | Armoured | 4 Core | 25 sq.mm. | KEI | 3262
Cable | Copper | Armoured | 1 Core | 35 sq.mm. | KEI | 1214
Cable | Copper | Armoured | 2 Core | 35 sq.mm. | KEI | 2297
Cable | Copper | Armoured | 3 Core | 35 sq.mm. | KEI | 3397
Cable | Copper | Armoured | 3.5 Core | 35 sq.mm. | KEI | 3914
Cable | Copper | Armoured | 4 Core | 35 sq.mm. | KEI | 4503
Cable | Copper | Armoured | 1 Core | 50 sq.mm. | KEI | 1690
Cable | Copper | Armoured | 2 Core | 50 sq.mm. | KEI | 3238
Cable | Copper | Armoured | 3 Core | 50 sq.mm. | KEI | 4793
Cable | Copper | Armoured | 3.5 Core | 50 sq.mm. | KEI | 5579
Cable | Copper | Armoured | 4 Core | 50 sq.mm. | KEI | 6379
Cable | Copper | Armoured | 1 Core | 70 sq.mm. | KEI | 2324
Cable | Copper | Armoured | 2 Core | 70 sq.mm. | KEI | 4490
Cable | Copper | Armoured | 3 Core | 70 sq.mm. | KEI | 6672
Cable | Copper | Armoured | 3.5 Core | 70 sq.mm. | KEI | 7766
Cable | Copper | Armoured | 4 Core | 70 sq.mm. | KEI | 8862
Cable | Copper | Armoured | 1 Core | 95 sq.mm. | KEI | 3097
Cable | Copper | Armoured | 2 Core | 95 sq.mm. | KEI | 6041
Cable | Copper | Armoured | 3 Core | 95 sq.mm. | KEI | 8986
Cable | Copper | Armoured | 3.5 Core | 95 sq.mm. | KEI | 10555
Cable | Copper | Armoured | 4 Core | 95 sq.mm. | KEI | 11955
Cable | Copper | Armoured | 1 Core | 120 sq.mm. | KEI | 3876
Cable | Copper | Armoured | 2 Core | 120 sq.mm. | KEI | 7597
Cable | Copper | Armoured | 3 Core | 120 sq.mm. | KEI | 11314
Cable | Copper | Armoured | 3.5 Core | 120 sq.mm. | KEI | 13503
Cable | Copper | Armoured | 4 Core | 120 sq.mm. | KEI | 15052
Cable | Copper | Armoured | 1 Core | 150 sq.mm. | KEI | 4814
Cable | Copper | Armoured | 2 Core | 150 sq.mm. | KEI | 9469
Cable | Copper | Armoured | 3 Core | 150 sq.mm. | KEI | 14124
Cable | Copper | Armoured | 3.5 Core | 150 sq.mm. | KEI | 16303
Cable | Copper | Armoured | 4 Core | 150 sq.mm. | KEI | 18786
Cable | Copper | Armoured | 1 Core | 185 sq.mm. | KEI | 5921
Cable | Copper | Armoured | 2 Core | 185 sq.mm. | KEI | 11652
Cable | Copper | Armoured | 3 Core | 185 sq.mm. | KEI | 17393
Cable | Copper | Armoured | 3.5 Core | 185 sq.mm. | KEI | 20352
Cable | Copper | Armoured | 4 Core | 185 sq.mm. | KEI | 23141
Cable | Copper | Armoured | 1 Core | 240 sq.mm. | KEI | 7628
Cable | Copper | Armoured | 2 Core | 240 sq.mm. | KEI | 15066
Cable | Copper | Armoured | 3 Core | 240 sq.mm. | KEI | 22476
Cable | Copper | Armoured | 3.5 Core | 240 sq.mm. | KEI | 26210
Cable | Copper | Armoured | 4 Core | 240 sq.mm. | KEI | 29934
Cable | Copper | Armoured | 1 Core | 300 sq.mm. | KEI | 9497
Cable | Copper | Armoured | 2 Core | 300 sq.mm. | KEI | 18772
Cable | Copper | Armoured | 3 Core | 300 sq.mm. | KEI | 28045
Cable | Copper | Armoured | 3.5 Core | 300 sq.mm. | KEI | 32734
Cable | Copper | Armoured | 4 Core | 300 sq.mm. | KEI | 37400
Cable | Copper | Armoured | 1 Core | 400 sq.mm. | KEI | 12614
Cable | Copper | Armoured | 2 Core | 400 sq.mm. | KEI | 24955
Cable | Copper | Armoured | 3 Core | 400 sq.mm. | KEI | 37328
Cable | Copper | Armoured | 3.5 Core | 400 sq.mm. | KEI | 43279
Cable | Copper | Armoured | 4 Core | 400 sq.mm. | KEI | 49979
Cable | Copper | Armoured | 1 Core | 500 sq.mm. | KEI | 15697
Cable | Copper | Armoured | 1 Core | 630 sq.mm. | KEI | 19728
Cable | Copper | Armoured | 1 Core | 800 sq.mm. | KEI | 24976
Cable | Copper | Armoured | 1 Core | 1000 sq.mm. | KEI | 31128
Cable | Copper | Armoured | 2 Core | 4 sq.mm. | Gloster | 404 |  | PRICE LIST NO : GCL/LTCuP/JAN-25
Cable | Copper | Armoured | 3 Core | 4 sq.mm. | Gloster | 541
Cable | Copper | Armoured | 4 Core | 4 sq.mm. | Gloster | 693
Cable | Copper | Armoured | 2 Core | 6 sq.mm. | Gloster | 569
Cable | Copper | Armoured | 3 Core | 6 sq.mm. | Gloster | 780
Cable | Copper | Armoured | 4 Core | 6 sq.mm. | Gloster | 1020
Cable | Copper | Armoured | 2 Core | 10 sq.mm. | Gloster | 904
Cable | Copper | Armoured | 3 Core | 10 sq.mm. | Gloster | 1269
Cable | Copper | Armoured | 4 Core | 10 sq.mm. | Gloster | 1620
Cable | Copper | Armoured | 1 Core | 16 sq.mm. | Gloster | 771
Cable | Copper | Armoured | 2 Core | 16 sq.mm. | Gloster | 1340
Cable | Copper | Armoured | 3 Core | 16 sq.mm. | Gloster | 1857
Cable | Copper | Armoured | 4 Core | 16 sq.mm. | Gloster | 2396
Cable | Copper | Armoured | 1 Core | 25 sq.mm. | Gloster | 1127
Cable | Copper | Armoured | 2 Core | 25 sq.mm. | Gloster | 2174
Cable | Copper | Armoured | 3 Core | 25 sq.mm. | Gloster | 2968
Cable | Copper | Armoured | 3.5 Core | 25 sq.mm. | Gloster | 3557
Cable | Copper | Armoured | 4 Core | 25 sq.mm. | Gloster | 3912
Cable | Copper | Armoured | 1 Core | 35 sq.mm. | Gloster | 1530
Cable | Copper | Armoured | 2 Core | 35 sq.mm. | Gloster | 2979
Cable | Copper | Armoured | 3 Core | 35 sq.mm. | Gloster | 4180
Cable | Copper | Armoured | 3.5 Core | 35 sq.mm. | Gloster | 4774
Cable | Copper | Armoured | 4 Core | 35 sq.mm. | Gloster | 5550
Cable | Copper | Armoured | 1 Core | 50 sq.mm. | Gloster | 2069
Cable | Copper | Armoured | 2 Core | 50 sq.mm. | Gloster | 3891
Cable | Copper | Armoured | 3 Core | 50 sq.mm. | Gloster | 5650
Cable | Copper | Armoured | 3.5 Core | 50 sq.mm. | Gloster | 6650
Cable | Copper | Armoured | 4 Core | 50 sq.mm. | Gloster | 7530
Cable | Copper | Armoured | 1 Core | 70 sq.mm. | Gloster | 2906
Cable | Copper | Armoured | 2 Core | 70 sq.mm. | Gloster | 5780
Cable | Copper | Armoured | 3 Core | 70 sq.mm. | Gloster | 8250
Cable | Copper | Armoured | 3.5 Core | 70 sq.mm. | Gloster | 9550
Cable | Copper | Armoured | 4 Core | 70 sq.mm. | Gloster | 10870
Cable | Copper | Armoured | 1 Core | 95 sq.mm. | Gloster | 3862
Cable | Copper | Armoured | 2 Core | 95 sq.mm. | Gloster | 7987
Cable | Copper | Armoured | 3 Core | 95 sq.mm. | Gloster | 11440
Cable | Copper | Armoured | 3.5 Core | 95 sq.mm. | Gloster | 13100
Cable | Copper | Armoured | 4 Core | 95 sq.mm. | Gloster | 15100
Cable | Copper | Armoured | 1 Core | 120 sq.mm. | Gloster | 4859
Cable | Copper | Armoured | 2 Core | 120 sq.mm. | Gloster | 9524
Cable | Copper | Armoured | 3 Core | 120 sq.mm. | Gloster | 14028
Cable | Copper | Armoured | 3.5 Core | 120 sq.mm. | Gloster | 17229
Cable | Copper | Armoured | 4 Core | 120 sq.mm. | Gloster | 18814
Cable | Copper | Armoured | 1 Core | 150 sq.mm. | Gloster | 6045
Cable | Copper | Armoured | 2 Core | 150 sq.mm. | Gloster | 11924
Cable | Copper | Armoured | 3 Core | 150 sq.mm. | Gloster | 17840
Cable | Copper | Armoured | 3.5 Core | 150 sq.mm. | Gloster | 20842
Cable | Copper | Armoured | 4 Core | 150 sq.mm. | Gloster | 23899
Cable | Copper | Armoured | 1 Core | 185 sq.mm. | Gloster | 7432
Cable | Copper | Armoured | 2 Core | 185 sq.mm. | Gloster | 14760
Cable | Copper | Armoured | 3 Core | 185 sq.mm. | Gloster | 22676
Cable | Copper | Armoured | 3.5 Core | 185 sq.mm. | Gloster | 26532
Cable | Copper | Armoured | 4 Core | 185 sq.mm. | Gloster | 30290
Cable | Copper | Armoured | 1 Core | 240 sq.mm. | Gloster | 9549
Cable | Copper | Armoured | 2 Core | 240 sq.mm. | Gloster | 19015
Cable | Copper | Armoured | 3 Core | 240 sq.mm. | Gloster | 29456
Cable | Copper | Armoured | 3.5 Core | 240 sq.mm. | Gloster | 34247
Cable | Copper | Armoured | 4 Core | 240 sq.mm. | Gloster | 39075
Cable | Copper | Armoured | 1 Core | 300 sq.mm. | Gloster | 11905
Cable | Copper | Armoured | 2 Core | 300 sq.mm. | Gloster | 24084
Cable | Copper | Armoured | 3 Core | 300 sq.mm. | Gloster | 37126
Cable | Copper | Armoured | 3.5 Core | 300 sq.mm. | Gloster | 42935
Cable | Copper | Armoured | 4 Core | 300 sq.mm. | Gloster | 49687
Cable | Copper | Armoured | 1 Core | 400 sq.mm. | Gloster | 15562
Cable | Copper | Armoured | 2 Core | 400 sq.mm. | Gloster | 32762
Cable | Copper | Armoured | 3 Core | 400 sq.mm. | Gloster | 47685
Cable | Copper | Armoured | 3.5 Core | 400 sq.mm. | Gloster | 54266
Cable | Copper | Armoured | 4 Core | 400 sq.mm. | Gloster | 66427
Cable | Copper | Armoured | 1 Core | 500 sq.mm. | Gloster | 19674
Cable | Copper | Armoured | 1 Core | 630 sq.mm. | Gloster | 24788
Cable | Copper | Armoured | 1 Core | 800 sq.mm. | Gloster | 31457
Cable | Copper | Armoured | 1 Core | 1000 sq.mm. | Gloster | 39237
Cable | Copper | Armoured | 2 Core | 1.5 sq.mm. | Polycab | 211 |  | PRICE LIST DATED: 2ND JAN
Cable | Copper | Armoured | 3 Core | 1.5 sq.mm. | Polycab | 269
Cable | Copper | Armoured | 4 Core | 1.5 sq.mm. | Polycab | 332
Cable | Copper | Armoured | 2 Core | 2.5 sq.mm. | Polycab | 299
Cable | Copper | Armoured | 3 Core | 2.5 sq.mm. | Polycab | 385
Cable | Copper | Armoured | 4 Core | 2.5 sq.mm. | Polycab | 498
Cable | Copper | Armoured | 2 Core | 4 sq.mm. | Polycab | 404
Cable | Copper | Armoured | 3 Core | 4 sq.mm. | Polycab | 541
Cable | Copper | Armoured | 4 Core | 4 sq.mm. | Polycab | 693
Cable | Copper | Armoured | 2 Core | 6 sq.mm. | Polycab | 569
Cable | Copper | Armoured | 3 Core | 6 sq.mm. | Polycab | 780
Cable | Copper | Armoured | 4 Core | 6 sq.mm. | Polycab | 1020
Cable | Copper | Armoured | 2 Core | 10 sq.mm. | Polycab | 904
Cable | Copper | Armoured | 3 Core | 10 sq.mm. | Polycab | 1269
Cable | Copper | Armoured | 4 Core | 10 sq.mm. | Polycab | 1620
Cable | Copper | Armoured | 2 Core | 16 sq.mm. | Polycab | 1340
Cable | Copper | Armoured | 3 Core | 16 sq.mm. | Polycab | 1857
Cable | Copper | Armoured | 4 Core | 16 sq.mm. | Polycab | 2396
Cable | Copper | Armoured | 1 Core | 25 sq.mm. | Polycab | 1169
Cable | Copper | Armoured | 3 Core | 25 sq.mm. | Polycab | 2968
Cable | Copper | Armoured | 3.5 Core | 25 sq.mm. | Polycab | 3557
Cable | Copper | Armoured | 4 Core | 25 sq.mm. | Polycab | 3912
Cable | Copper | Armoured | 5 Core | 25 sq.mm. | Polycab | 5676
Cable | Copper | Armoured | 1 Core | 35 sq.mm. | Polycab | 1587
Cable | Copper | Armoured | 3 Core | 35 sq.mm. | Polycab | 4180
Cable | Copper | Armoured | 3.5 Core | 35 sq.mm. | Polycab | 4774
Cable | Copper | Armoured | 4 Core | 35 sq.mm. | Polycab | 5550
Cable | Copper | Armoured | 5 Core | 35 sq.mm. | Polycab | 7686
Cable | Copper | Armoured | 1 Core | 50 sq.mm. | Polycab | 2146
Cable | Copper | Armoured | 3 Core | 50 sq.mm. | Polycab | 5650
Cable | Copper | Armoured | 3.5 Core | 50 sq.mm. | Polycab | 6650
Cable | Copper | Armoured | 4 Core | 50 sq.mm. | Polycab | 7530
Cable | Copper | Armoured | 5 Core | 50 sq.mm. | Polycab | 10524
Cable | Copper | Armoured | 1 Core | 70 sq.mm. | Polycab | 3014
Cable | Copper | Armoured | 3 Core | 70 sq.mm. | Polycab | 8250
Cable | Copper | Armoured | 3.5 Core | 70 sq.mm. | Polycab | 9550
Cable | Copper | Armoured | 4 Core | 70 sq.mm. | Polycab | 10870
Cable | Copper | Armoured | 1 Core | 95 sq.mm. | Polycab | 4005
Cable | Copper | Armoured | 3 Core | 95 sq.mm. | Polycab | 11440
Cable | Copper | Armoured | 3.5 Core | 95 sq.mm. | Polycab | 13100
Cable | Copper | Armoured | 4 Core | 95 sq.mm. | Polycab | 15100
Cable | Copper | Armoured | 1 Core | 120 sq.mm. | Polycab | 5040
Cable | Copper | Armoured | 3 Core | 120 sq.mm. | Polycab | 14028
Cable | Copper | Armoured | 3.5 Core | 120 sq.mm. | Polycab | 17229
Cable | Copper | Armoured | 4 Core | 120 sq.mm. | Polycab | 18814
Cable | Copper | Armoured | 1 Core | 150 sq.mm. | Polycab | 6270
Cable | Copper | Armoured | 3 Core | 150 sq.mm. | Polycab | 17840
Cable | Copper | Armoured | 3.5 Core | 150 sq.mm. | Polycab | 20842
Cable | Copper | Armoured | 4 Core | 150 sq.mm. | Polycab | 23899
Cable | Copper | Armoured | 1 Core | 185 sq.mm. | Polycab | 7708
Cable | Copper | Armoured | 3 Core | 185 sq.mm. | Polycab | 22676
Cable | Copper | Armoured | 3.5 Core | 185 sq.mm. | Polycab | 26532
Cable | Copper | Armoured | 4 Core | 185 sq.mm. | Polycab | 30290
Cable | Copper | Armoured | 1 Core | 240 sq.mm. | Polycab | 9904
Cable | Copper | Armoured | 3 Core | 240 sq.mm. | Polycab | 29456
Cable | Copper | Armoured | 3.5 Core | 240 sq.mm. | Polycab | 34247
Cable | Copper | Armoured | 4 Core | 240 sq.mm. | Polycab | 39075
Cable | Copper | Armoured | 1 Core | 300 sq.mm. | Polycab | 12348
Cable | Copper | Armoured | 3 Core | 300 sq.mm. | Polycab | 37126
Cable | Copper | Armoured | 3.5 Core | 300 sq.mm. | Polycab | 42935
Cable | Copper | Armoured | 4 Core | 300 sq.mm. | Polycab | 49687
Cable | Copper | Armoured | 1 Core | 400 sq.mm. | Polycab | 16141
Cable | Copper | Armoured | 3 Core | 400 sq.mm. | Polycab | 47685
Cable | Copper | Armoured | 3.5 Core | 400 sq.mm. | Polycab | 54266
Cable | Copper | Armoured | 4 Core | 400 sq.mm. | Polycab | 66427

## 10
Item | Method | Size | Core | Rate | Description | GS
Laying | On Wall / surface with Saddles / clamps | upto 25 sq.mm. | 2 Core | 57 | Laying of cable upto 2 core 25 sqmm on wall/surface incl. S & F MS saddles with earthing attachment in 10 SWG GI (Hot Dip) Wire, making holes etc. as necy. mending good damages and painting | PWD/GS -F-1:2 (a)
Laying | On Wall / surface with Saddles / clamps | upto 25 sq.mm. | 3 / 4 Core | 60 | Laying of cable upto 3/4 core 25 sqmm on wall/surface incl. S & F MS saddles with earthing attachment in 10 SWG GI (Hot Dip) Wire, making holes etc. as necy. mending good damages and painting | PWD/GS -F-1:2 (b)
Laying | On Wall / surface with Saddles / clamps | above 25 sqmm and upto 50 sqmm | 3 / 3.5 / 4 Core | 71 | Laying of cable from 3/3½/4 core 35 sqmm to 50 sqmm on wall/surface incl. S & F MS saddles with earthing attachment in 2 x 10 SWG GI (Hot Dip) Wire, making holes etc. as necy., mending good damages and painting | PWD/GS -F-1:2 (c)
Laying | On Wall / surface with Saddles / clamps | above 50 sqmm and upto 90 sqmm | 3 / 3.5 / 4 Core | 83 | Laying of cable above 3½/4 core 50 sqmm and upto 3½ core 90 sqmm on wall/surface including S & F MS clams with earthing attachment in 2 x 10 SWG GI (Hot Dip) Wire, making hole etc. as necy., mending good damages and painting | PWD/GS -F-1:2 (d)
Laying | On Wall / surface with Saddles / clamps | above 90 sqmm and upto 150 sqmm | 3.5 / 4 Core | 86 | Laying of cable above 3½ core 90 sqmm and upto 3½ core 150 sqmm on wall/surface including S & F MS clams with earthing attachment in 2 x 10 SWG GI (Hot Dip) Wire, making hole etc. as necy., mending good damages and painting | PWD/GS -F-1:2 (e)
Laying | through RCC/Hume/GI Pipe/open masonary trench | upto 50 sqmm | 1 / 2 / 3 / 3.5 /4 core | 43 | Laying only Cable upto 50 sqmm through existing RCC/Hume/ GI Pipe/open masonary trench for single, 2, 3, 3½ & 4 core | PWD/GS -F-1:3 (a)
Laying | through RCC/Hume/GI Pipe/open masonary trench | above 50 sqmm | 1 / 2 / 3 / 3.5 /4 core | 60 | Laying only Cable above 50 sqmm but not exceeding 400sqmm through existing RCC/ Hume/GI Pipe/open masonary trench for single, 2, 3, 3½ and 4 core | PWD/GS -F-1:3 (b)
Laying | on Pole with Clamps | upto 400 sqmm | 1 / 2 / 3 / 3.5 /4 core | 67 | Fixing of Cable along the lenth of O.H. pole incl. S & F MS pole clamps fabricated from 25 mm x 6 mm MS flat incl. painting | PWD/GS -F-1:4
Laying | through Underground Trech | upto 35 sqmm | one cable | 162 | Laying of one cable upto 35 sqmm in underground trench 460 mm wide x 760 mm average depth, with brick protection on the top of the cable with 8 (eight) Nos. bricks per metre, including filling the space between the brick & cable and also the trench with shifted soil, leveling up and restoring surface duly rammed | PWD/GS -F-2:1(a)
Laying | through Underground Trech | above 35 sqmm and upto 185 sqmm | one cable | 172 | Laying of one cable above 35 sqmm and upto 185 sqmm in underground trench 460mm wide x 760mm average depth, with brick protection on the top of the cable with 8 (eight) Nos. bricks per Mtr. including filling the space between the bricks and cable and also the trenchwith shifted soil, leveling up and restoring surface duly rammed | PWD/GS -F-2:1(b)
Laying | through Underground Trech | above 185 sqmm | one cable | 187 | Laying of one cable above 185 sqmm in underground trench 460mm wide x 760mm average depth, with brick protection on the top of the cable with 8 (eight) Nos. bricks per Mtr. including filling the space between the bricks and cable and also the trench with shifted soil, leveling up and restoring surface duly rammed | PWD/GS -F-2:1(c)
Laying | through Underground Trech | upto 35 sqmm | two cables | 301 | Laying of two cables upto 35 sqmm in an underground trench in single tier formation (horizontal), the trench size : 680 mm x 760 mm average depth, with brick protection on the top of each cable 8 (eight) Nos. bricks per Mtr. and 4 (four) Nos. bricks per Mtr. as separator between the bricks and cables and also trench to be filled up with shifted soil, levelling up and restoring surface duly rammed | PWD/GS -F-2:2(a)
Laying | through Underground Trech | above 35 sqmm and upto 185 sqmm | two cables | 315 | Laying of two cables above 35 sqmm and upto 185 sqmm in an underground trench in single tier formation (horizontal), the trench size : 680 mm x 760 mm average depth, with brick protection on the top of each cable 8 (eight) Nos. bricks per Mtr. and 4 (four) Nos. bricks per Mtr. as separator between the bricks and cables and also trench to be filled up with shifted soil, levelling up and restoring surface duly rammed | PWD/GS -F-2:2(b)
Laying | through Underground Trech | above 185 sqmm | two cables | 337 | Laying of two cables above 185 sqmm in an underground trench in single tier formation (horizontal), the trench size : 680 mm x 760 mm average depth, with brick protection on the top of each cable 8 (eight) Nos. bricks per Mtr. and 4 (four) Nos. bricks per Mtr. as separator between the bricks and cables and also trench to be filled up with shifted soil, levelling up and restoring surface duly rammed | PWD/GS -F-2:2(c)
Laying | through Underground Trech | upto 35 sqmm | three cables | 438 | Laying of three cables upto 35 sqmm in an underground trench in single tier formation (horizontal) the trench size : 915 mm x 760 mm average depth with brick protection on the top of each cable with 8 nos. bricks per Mtr. and 4 nos. bricks per mtr. as separator between the cables including filling the space between the bricks and cables and also the trench with shifted soil, levelling up and restoring surface duly rammed | PWD/GS -F-2:3(a)
Laying | through Underground Trech | above 35 sqmm and upto 185 sqmm | three cables | 458 | Laying of three cables above 35 sqmm and upto 185 sqmm in an underground trench in single tier formation (horizontal) the trench size : 915 mm x 760 mm average depth with brick protection on the top of each cable with 8 nos. bricks per Mtr. and 4 nos. bricks per mtr. as separator between every two cables including filling the space between the bricks and cables and also the trench with shifted soil, levelling up and restoring surface duly rammed | PWD/GS -F-3:3(b)
Laying | through Underground Trech | above 185 sqmm | three cables | 487 | Laying of three cables above 185 sqmm in an underground trench in single tier formation (horizontal) the trench size : 915 mm x 760 mm average depth with brick protection on the top of each cable with 8 nos. bricks per Mtr. and 4 nos. bricks per mtr. as separator between every two cables including filling the space between the bricks and cables and also the trench with shifted soil, levelling up and restoring surface duly rammed | PWD/GS -F-3:3(b)
Laying | through Masonry Trench | upto 150 sqmm | one cable | 96 | Laying of one cable upto 150 sqmm through existing covered masonry trench incl. taking out RC covers, setting them in order, mending good the damages filling the trench with fine dry sand incl. supplying sand | PWD/GS -F-3:4(a)
Laying | through Masonry Trench | above 150 sqmm and upto 300 sqmm | one cable | 136 | Laying of one cable above 150 sqmm and upto 300 sqmm through existing covered masonry trench incl. taking out RC covers, setting them in order, mending good the damages filling the trench with fine dry sand incl. supplying sand | PWD/GS -F-3:4(b)
Laying | through Masonry Trench | above 300 sqmm | one cable | 156 | Laying of one cable above 300 sqmm through existing covered masonry trench incl. taking out RC covers, setting them in order, mending good the damages filling the trench with fine dry sand incl. supplying sand | PWD/GS -F-3:4(c)
Laying | through Floor/ Pavement/Wall | upto 35 sqmm | one cable | 127 | Laying of cable as below, after cutting floor/pavement/wall/ and making holes incl., embedding the cable at an average depth as below and mending good the damages to original finish incl. removing the rubbish - From 2.5 sqmm to 35 sqmm at an average depth of 75 mm in floor/pavement/wall etc | PWD/GS -F-3:5(i)
Laying | through Floor/ Pavement/Wall | above 35 sqmm and upto 95 sqmm | one cable | 159 | Laying of cable as below, after cutting floor/pavement/wall/ and making holes incl., embedding the cable at an average depth as below and mending good the damages to original finish incl. removing the rubbish -Above 35 sqmm to 95 sqmm at an average depth of 100 mm in floor/pavement/wall etc. | PWD/GS -F-3:5(ii)
Laying | through Floor/ Pavement/Wall | above 95 sqmm | one cable | 181 | Laying of cable as below, after cutting floor/pavement/wall/ and making holes incl., embedding the cable at an average depth as below and mending good the damages to original finish incl. removing the rubbish - Above 95 sqmm at an average depth of 100 mm in floor/pavement/wall etc. | PWD/GS -F-3:5(iii)
Laying | on Cable Tray | upto 50 sqmm | one cable | 11 | Laying of cable as below, on existing Cable Tray and binding with suitable size GI wire. - Up to 50 sqmm | PWD/GS -F-3:6(i)
Laying | on Cable Tray | above 50 sqmm and upto 150 sqmm | one cable | 15 | Laying of cable as below, on existing Cable Tray and binding with suitable size GI wire. - From 70sqmm to 150sqmm | PWD/GS -F-3:6(ii)
Laying | on Cable Tray | above 150 sqmm | one cable | 19 | Laying of cable as below, on existing Cable Tray and binding with suitable size GI wire. - Above 150 sqmm | PWD/GS -F-3:6(iii)

## 11
Item | Type | Current Rating | Release | Company | Rate
ACB | MDO | 630A | Thermo-Magnetic | L&T | 163870
ACB | MDO | 800A | Thermo-Magnetic | L&T | 163870
ACB | MDO | 1000A | Thermo-Magnetic | L&T | 173190
ACB | MDO | 1250A | Thermo-Magnetic | L&T | 192720
ACB | MDO | 1600A | Thermo-Magnetic | L&T | 211960
ACB | MDO | 2000A | Thermo-Magnetic | L&T | 258160
ACB | MDO | 630A | Thermo-Magnetic | Havells | 39
ACB | MDO | 800A | Thermo-Magnetic | Havells | 49
ACB | MDO | 1000A | Thermo-Magnetic | Havells | 59
ACB | MDO | 1250A | Thermo-Magnetic | Havells | 69
ACB | MDO | 1600A | Thermo-Magnetic | Havells | 79
ACB | MDO | 2000A | Thermo-Magnetic | Havells | 89
ACB | MDO | 630A | Thermo-Magnetic | ABB | 51
ACB | MDO | 800A | Thermo-Magnetic | ABB | 61
ACB | MDO | 1000A | Thermo-Magnetic | ABB | 71
ACB | MDO | 1250A | Thermo-Magnetic | ABB | 81
ACB | MDO | 1600A | Thermo-Magnetic | ABB | 91
ACB | MDO | 2000A | Thermo-Magnetic | ABB | 101
ACB | MDO | 630A | Thermo-Magnetic | Siemens | 217310
ACB | MDO | 800A | Thermo-Magnetic | Siemens | 230935
ACB | MDO | 1000A | Thermo-Magnetic | Siemens | 235045
ACB | MDO | 1250A | Thermo-Magnetic | Siemens | 264585
ACB | MDO | 1600A | Thermo-Magnetic | Siemens | 289165
ACB | MDO | 2000A | Thermo-Magnetic | Siemens | 369385
ACB | MDO | 630A | Thermo-Magnetic | Legrand | 65
ACB | MDO | 800A | Thermo-Magnetic | Legrand | 75
ACB | MDO | 1000A | Thermo-Magnetic | Legrand | 85
ACB | MDO | 1250A | Thermo-Magnetic | Legrand | 95
ACB | MDO | 1600A | Thermo-Magnetic | Legrand | 105
ACB | MDO | 2000A | Thermo-Magnetic | Legrand | 115

## 12
Item | Type | Using | Wiring | Avg. Run | Rate | Description | GS
Point Switch Board | Flush / Piano key | Polythen pipe | Embedded in wall | Average run 6 mtr | 780 | Distn. wiring in 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed single core stranded copper wire (Brand approved by EIC) in 19 mm bore, 3 mm thick polythen pipe complete with all accessories embedded in wall to light/fan/call bell points with Piano key type switch (Anchor make) fixed on sheet metal (16 SWG) switch board with bakelite/perspex (wall matching colour) top cover (3 mm thick) flushed in wall incl. mending good damages to original finish - 2x22/0.3 (Ph. & N) and 1x22/0.3 as ECC | PWD/GS -E-9 : 2 (a)(i)
Point Switch Board | Flush / Piano key | Polythen pipe | Embedded in wall | Average run 7 mtr | 874 |  | PWD/GS -E-9 : 2 (a)(ii)
Point Switch Board | Flush / Piano key | Polythen pipe | Embedded in wall | Average run 8 mtr | 967 |  | PWD/GS -E-9 : 2 (a)(iii)
Point Switch Board | Flush / Piano key | Polythen pipe | Embedded in wall | Average run 9 mtr | 1061 |  | PWD/GS -E-9 : 2 (a)(iv)
Point Switch Board | Flush / Piano key | Polythen pipe | Embedded in wall | Average run 10 mtr | 1154 |  | PWD/GS -E-9 : 2 (a)(v)
Point Switch Board | Flush / Piano key | Polythen pipe | Embedded in wall | Average run 11 mtr | 1248 |  | PWD/GS -E-9 : 2 (a)(vi)
Point Switch Board | Flush / Piano key | Polythen pipe | Embedded in wall | Average run 12 mtr | 1341 |  | PWD/GS -E-9 : 2 (a)(vii)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping and board both on surface | Average run 5 mtr | 577 | Distribution wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in suitable size PVC casing-capping (Precision make) with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, incl. necy. PVC clips, fittings etc. to light/fan/call bell point with piano key type switch (Anchor make) fixed on sheet steel fabricated switch board with Perspex/bakelite top cover on wall incl. necy. connections and making earthing attachment and mending good damages to building works. [PVC casing-capping and Switch board both on surface] | PWD/GS -E-11 : 2 (a)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping and board both on surface | Average run 6 mtr | 650 |  | PWD/GS -E-11 : 2 (b)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping and board both on surface | Average run 8 mtr | 796 |  | PWD/GS -E-11 : 2 (c)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping and board both on surface | Average run 9 mtr | 870 |  | PWD/GS -E-11 : 2 (d)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping and board both on surface | Average run 10 mtr | 943 |  | PWD/GS -E-11 : 2 (e)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping and board both on surface | Average run 11 mtr | 1016 |  | PWD/GS -E-11 : 2 (f)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping and board both on surface | Average run 12 mtr | 1089 |  | PWD/GS -E-11 : 2 (g)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping on surface and board concealed | Average run 5 mtr | 609 | Distribution wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in suitable size PVC casing-capping (Precision make) with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, incl. necy. PVC clips, fittings etc. to light/fan/call bell point with piano key type switch (Anchor make) fixed on sheet steel fabricated switch board with Perspex/bakelite top cover on wall incl. necy. connections and making earthing attachment and mending good damages to building works. [PVC casing-capping on surface and Switch board concealed] | PWD/GS -E-11 : 4 (a)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping on surface and board concealed | Average run 6 mtr | 686 |  | PWD/GS -E-11 : 4 (b)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping on surface and board concealed | Average run 8 mtr | 839 |  | PWD/GS -E-11 : 4 (c)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping on surface and board concealed | Average run 9 mtr | 916 |  | PWD/GS -E-11 : 4 (d)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping on surface and board concealed | Average run 10 mtr | 993 |  | PWD/GS -E-11 : 4 (e)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping on surface and board concealed | Average run 11 mtr | 1069 |  | PWD/GS -E-11 : 4 (f)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping on surface and board concealed | Average run 12 mtr | 1146 |  | PWD/GS -E-11 : 4 (g)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping on Wall and vertical run & board both concealed | Average run 5 mtr | 572 | Distribution wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in suitable size PVC casing-capping (Precision make) [for horizontal run & ceiling portion] and partly in 19mm bore, 3mm thick polythene concealed pipe [for vertical run embedded in wall only], with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, incl. necy. PVC clips, fittings etc. to light/fan/call bell points with piano key type switch (Anchor make) fixed on sheet steel fabricated switch board with Perspex/bakelite top cover on wall incl. necy. connections and making earthing attachment and mending good damages to building works [PVC casing-capping on Wall and vertical run & switch box both concealed] | PWD/GS -E-13 : 8 (a)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping on Wall and vertical run & board both concealed | Average run 6 mtr | 634 |  | PWD/GS -E-13 : 8 (b)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping on Wall and vertical run & board both concealed | Average run 8 mtr | 759 |  | PWD/GS -E-13 : 8 (c)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping on Wall and vertical run & board both concealed | Average run 9 mtr | 821 |  | PWD/GS -E-13 : 8 (d)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping on Wall and vertical run & board both concealed | Average run 10 mtr | 883 |  | PWD/GS -E-13 : 8 (e)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping on Wall and vertical run & board both concealed | Average run 11 mtr | 946 |  | PWD/GS -E-13 : 8 (f)
Point Switch Board | Flush / Piano key | Casing-Capping | Casing-capping on Wall and vertical run & board both concealed | Average run 12 mtr | 1008 |  | PWD/GS -E-13 : 8 (g)
Point Switch Board | Flush / Piano key | Casing-Capping | Only casing-capping on ceiling and remaining portion concealed | Average run 5 mtr | 740 | Distribution wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (approved make) for ECC in 19 mm bore, 3 mm thick polythene pipe complete with all accessories embedded in wall for horizontal & vertical runs and in suitable size PVC casing-capping (Precision make) for ceiling portion only, incl. necy. PVC clips, fittings etc. to light/fan/call bell point with piano key type switch (Anchor make) fixed on sheet steel fabricated switch board with Perspex/bakelite top cover on wall incl. necy. connections and making earthing attachment and mending good damages to building works [only PVC casing-capping on ceiling and remaining portion concealed] | PWD/GS -E-13 : 9 (a)
Point Switch Board | Flush / Piano key | Casing-Capping | Only casing-capping on ceiling and remaining portion concealed | Average run 6 mtr | 843 |  | PWD/GS -E-13 : 9 (b)
Point Switch Board | Flush / Piano key | Casing-Capping | Only casing-capping on ceiling and remaining portion concealed | Average run 8 mtr | 1048 |  | PWD/GS -E-13 : 9 (c)
Point Switch Board | Flush / Piano key | Casing-Capping | Only casing-capping on ceiling and remaining portion concealed | Average run 9 mtr | 1151 |  | PWD/GS -E-13 : 9 (d)
Point Switch Board | Flush / Piano key | Casing-Capping | Only casing-capping on ceiling and remaining portion concealed | Average run 10 mtr | 1253 |  | PWD/GS -E-13 : 9 (e)
Point Switch Board | Flush / Piano key | Casing-Capping | Only casing-capping on ceiling and remaining portion concealed | Average run 11 mtr | 1356 |  | PWD/GS -E-13 : 9 (f)
Point Switch Board | Flush / Piano key | Casing-Capping | Only casing-capping on ceiling and remaining portion concealed | Average run 12 mtr | 1459 |  | PWD/GS -E-13 : 9 (g)
Point Switch Board | Flush / Piano key | Rigid Conduit | Conduit and board both on surface | Average run 5 mtr | 612 | Distribution wiring in 2 x 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in 20mm size PVC rigid conduit 'FR' (Precision make), with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, to light/fan/call bell points with Piano Key type switch fixed on MS CRC sheet metal (16 SWG) switch board cum JB on wall complete with 2 no. suitable size “Ph & N” copper bar incl. bakelite/Perspex (wall matching color) top cover 3 mm thick and incl. 175mmx100mmx65mm inspection box, making earthing attachment, painting the MS box and mending good the damages to original finish | PWD/GS -E-14 : 2 (a)
Point Switch Board | Flush / Piano key | Rigid Conduit | Conduit and board both on surface | Average run 6 mtr | 691 |  | PWD/GS -E-14 : 2 (b)
Point Switch Board | Flush / Piano key | Rigid Conduit | Conduit and board both on surface | Average run 8 mtr | 849 |  | PWD/GS -E-14 : 2 (c)
Point Switch Board | Flush / Piano key | Rigid Conduit | Conduit and board both on surface | Average run 9 mtr | 928 |  | PWD/GS -E-14 : 2 (d)
Point Switch Board | Flush / Piano key | Rigid Conduit | Conduit and board both on surface | Average run 10 mtr | 1007 |  | PWD/GS -E-14 : 2 (e)
Point Switch Board | Flush / Piano key | Rigid Conduit | Conduit and board both on surface | Average run 11 mtr | 1086 |  | PWD/GS -E-14 : 2 (f)
Point Switch Board | Flush / Piano key | Rigid Conduit | Conduit and board both on surface | Average run 12 mtr | 1165 |  | PWD/GS -E-14 : 2 (g)
Point Switch Board | Flush / Piano key | Rigid Conduit | Only Conduit on ceiling and remaining portion concealed | Average run 5 mtr | 693 | Distribution wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) partly in 20mm size PVC rigid conduit 'FR' (Precision make) [for ceiling portion only] and in 19mm bore, 3mm thick polythene pipe [for horizontal & vertical run embedded in wall], with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, to light/fan/call bell points with Piano Key type switch fixed on MS CRC sheet metal (16 SWG) switch board on wall complete with 2 no. “Ph & N” copper bar incl. bakelite/ Perspex top cover 3 mm thick and incl. 175x100x65mm inspection box, making earthing attachment, painting the MS box and mending good the damages to original finish [only PVC Rigid Conduit on ceiling and remaining portion concealed] | PWD/GS -E-15 : 5 (a)
Point Switch Board | Flush / Piano key | Rigid Conduit | Only Conduit on ceiling and remaining portion concealed | Average run 6 mtr | 793 |  | PWD/GS -E-15 : 5 (b)
Point Switch Board | Flush / Piano key | Rigid Conduit | Only Conduit on ceiling and remaining portion concealed | Average run 8 mtr | 992 |  | PWD/GS -E-15 : 5 (c)
Point Switch Board | Flush / Piano key | Rigid Conduit | Only Conduit on ceiling and remaining portion concealed | Average run 9 mtr | 1092 |  | PWD/GS -E-15 : 5 (d)
Point Switch Board | Flush / Piano key | Rigid Conduit | Only Conduit on ceiling and remaining portion concealed | Average run 10 mtr | 1191 |  | PWD/GS -E-15 : 5 (e)
Point Switch Board | Flush / Piano key | Rigid Conduit | Only Conduit on ceiling and remaining portion concealed | Average run 11 mtr | 1291 |  | PWD/GS -E-15 : 5 (f)
Point Switch Board | Flush / Piano key | Rigid Conduit | Only Conduit on ceiling and remaining portion concealed | Average run 12 mtr | 1391 |  | PWD/GS -E-15 : 5 (g)
Point Switch Board | Flush / Piano key | Rigid Conduit | Conduit only for horizontal run & above false ceiling and vertical run concealed | Average run 5 mtr | 685 | Distribution wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (approved make) partly in 20mm size PVC rigid conduit 'FR' (Brand approved by EIC) [for horizontal run & above false ceiling portion only] and in 19mm bore, 3mm thick polythene pipe [for vertical run embedded in wall], with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, to light/fan/call bell points with Piano Key type switch fixed on MS CRC sheet metal (16 SWG) switch board on wall complete with 2 no. “Ph & N” copper bar incl. bakelite/ Perspex top cover 3 mm thick and incl. 175x100x65mm inspection box, making earthing attachment, painting the MS box and mending good the damages to original finish [PVC Rigid Conduit only for horizontal run & above false ceiling and vertical run concealed] | PWD/GS -E-16 : 6 (a)
Point Switch Board | Flush / Piano key | Rigid Conduit | Conduit only for horizontal run & above false ceiling and vertical run concealed | Average run 6 mtr | 770 |  | PWD/GS -E-16 : 6 (b)
Point Switch Board | Flush / Piano key | Rigid Conduit | Conduit only for horizontal run & above false ceiling and vertical run concealed | Average run 8 mtr | 939 |  | PWD/GS -E-16 : 6 (c)
Point Switch Board | Flush / Piano key | Rigid Conduit | Conduit only for horizontal run & above false ceiling and vertical run concealed | Average run 9 mtr | 1023 |  | PWD/GS -E-16 : 6 (d)
Point Switch Board | Flush / Piano key | Rigid Conduit | Conduit only for horizontal run & above false ceiling and vertical run concealed | Average run 10 mtr | 1108 |  | PWD/GS -E-16 : 6 (e)
Point Switch Board | Flush / Piano key | Rigid Conduit | Conduit only for horizontal run & above false ceiling and vertical run concealed | Average run 11 mtr | 1192 |  | PWD/GS -E-16 : 6 (f)
Point Switch Board | Flush / Piano key | Rigid Conduit | Conduit only for horizontal run & above false ceiling and vertical run concealed | Average run 12 mtr | 1277 |  | PWD/GS -E-16 : 6 (g)
Point Switch Board | Modular type | Polythen pipe | Embedded in wall | Average run 6 mtr | 893 | Distn. wiring in 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed single core stranded copper wire (Brand approved by EIC) in 19 mm bore, 3 mm thick polythen pipe complete with all accessories embedded in wall to light/fan/call bell points with Modular type switch (Brand approved by EIC) fixed on Modular GI switch board with top cover plate flushed in wall incl. mending good damages to original finish - 2x22/0.3 (Ph. & N) and 1x22/0.3 as ECC | PWD/GS -E-20 : 1 (i)
Point Switch Board | Modular type | Polythen pipe | Embedded in wall | Average run 7 mtr | 993 |  | PWD/GS -E-20 : 1 (ii)
Point Switch Board | Modular type | Polythen pipe | Embedded in wall | Average run 8 mtr | 1093 |  | PWD/GS -E-20 : 1 (iii)
Point Switch Board | Modular type | Polythen pipe | Embedded in wall | Average run 9 mtr | 1193 |  | PWD/GS -E-20 : 1 (iv)
Point Switch Board | Modular type | Polythen pipe | Embedded in wall | Average run 10 mtr | 1292 |  | PWD/GS -E-20 : 1 (v)
Point Switch Board | Modular type | Polythen pipe | Embedded in wall | Average run 11 mtr | 1392 |  | PWD/GS -E-20 : 1 (vi)
Point Switch Board | Modular type | Polythen pipe | Embedded in wall | Average run 12 mtr | 1492 |  | PWD/GS -E-20 : 1 (vii)
Point Switch Board | Modular type | Casing-Capping | Casing-capping and board both on surface | Average run 5 mtr | 659 | Distribution wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in suitable size PVC casing-capping (Precision make) with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, incl. necy. fittings etc. to light/fan/call bell point with Modular type switch (Brand approved by EIC) fixed on Modular GI / PVC switch board with top cover plate on wall incl. mending good damages to original finish. [PVC casingcapping and Switch board both on surface] | PWD/GS -E-21 : 1 (a)
Point Switch Board | Modular type | Casing-Capping | Casing-capping and board both on surface | Average run 6 mtr | 733 |  | PWD/GS -E-21 : 1 (b)
Point Switch Board | Modular type | Casing-Capping | Casing-capping and board both on surface | Average run 8 mtr | 879 |  | PWD/GS -E-21 : 1 (c)
Point Switch Board | Modular type | Casing-Capping | Casing-capping and board both on surface | Average run 9 mtr | 952 |  | PWD/GS -E-21 : 1 (d)
Point Switch Board | Modular type | Casing-Capping | Casing-capping and board both on surface | Average run 10 mtr | 1025 |  | PWD/GS -E-21 : 1 (e)
Point Switch Board | Modular type | Casing-Capping | Casing-capping and board both on surface | Average run 11 mtr | 1098 |  | PWD/GS -E-21 : 1 (f)
Point Switch Board | Modular type | Casing-Capping | Casing-capping and board both on surface | Average run 12 mtr | 1171 |  | PWD/GS -E-21 : 1 (g)
Point Switch Board | Modular type | Casing-Capping | Casing-capping on surface and board concealed | Average run 5 mtr | 750 | Distribution wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in suitable size PVC casing-capping (Precision make) with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, incl. necy. fittings etc. to light/fan/call bell point with Modular type switch (Brand approved by EIC) fixed on Modular GI switch board with top cover plate flushed in wall incl. mending good damages to original finish [PVC casingcapping on surface and Switch board concealed] | PWD/GS -E-21 : 3 (a)
Point Switch Board | Modular type | Casing-Capping | Casing-capping on surface and board concealed | Average run 6 mtr | 827 |  | PWD/GS -E-21 : 3 (b)
Point Switch Board | Modular type | Casing-Capping | Casing-capping on surface and board concealed | Average run 8 mtr | 980 |  | PWD/GS -E-21 : 3 (c)
Point Switch Board | Modular type | Casing-Capping | Casing-capping on surface and board concealed | Average run 9 mtr | 1057 |  | PWD/GS -E-21 : 3 (d)
Point Switch Board | Modular type | Casing-Capping | Casing-capping on surface and board concealed | Average run 10 mtr | 1134 |  | PWD/GS -E-21 : 3 (e)
Point Switch Board | Modular type | Casing-Capping | Casing-capping on surface and board concealed | Average run 11 mtr | 1210 |  | PWD/GS -E-21 : 3 (f)
Point Switch Board | Modular type | Casing-Capping | Casing-capping on surface and board concealed | Average run 12 mtr | 1287 |  | PWD/GS -E-21 : 3 (g)
Point Switch Board | Modular type | Casing-Capping | Casing-capping on Wall and vertical run & board both concealed | Average run 5 mtr | 706 | Distribution wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in suitable size PVC casing-capping (Precision make) [for horizontal run & ceiling portion] and partly in 19mm bore, 3mm thick polythene concealed pipe [for vertical run embedded in wall only], with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, incl. necy. fittings etc. to light/fan/call bell points with Modular type switch (Brand approved by EIC) fixed on Modular GI switch board with top cover plate and 2 no. suitable size “Ph & N” copper bar & earthing attachment flushed in wall incl. mending good damages to original finish [PVC casing-capping on Wall and vertical & switch box both concealed] | PWD/GS -E-23 : 7 (a)
Point Switch Board | Modular type | Casing-Capping | Casing-capping on Wall and vertical run & board both concealed | Average run 6 mtr | 780 |  | PWD/GS -E-23 : 7 (b)
Point Switch Board | Modular type | Casing-Capping | Casing-capping on Wall and vertical run & board both concealed | Average run 8 mtr | 926 |  | PWD/GS -E-23 : 7 (c)
Point Switch Board | Modular type | Casing-Capping | Casing-capping on Wall and vertical run & board both concealed | Average run 9 mtr | 999 |  | PWD/GS -E-23 : 7 (d)
Point Switch Board | Modular type | Casing-Capping | Casing-capping on Wall and vertical run & board both concealed | Average run 10 mtr | 1072 |  | PWD/GS -E-23 : 7 (e)
Point Switch Board | Modular type | Casing-Capping | Casing-capping on Wall and vertical run & board both concealed | Average run 11 mtr | 1145 |  | PWD/GS -E-23 : 7 (f)
Point Switch Board | Modular type | Casing-Capping | Casing-capping on Wall and vertical run & board both concealed | Average run 12 mtr | 1219 |  | PWD/GS -E-23 : 7 (g)
Point Switch Board | Modular type | Casing-Capping | Only casing-capping on ceiling and remaining portion concealed | Average run 5 mtr | 807 | Distribution wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) for ECC in 19 mm bore, 3 mm thick polythene pipe complete with all accessories embedded in wall for horizontal & vertical runs and in suitable size PVC casing-capping (Precision make) for ceiling portion only, incl. necy. fittings etc. to light/fan/call bell point with Modular type switch (Brand approved by EIC) fixed on Modular GI switch board with top cover plate and 2 no. suitable size “Ph & N” copper bar & earthing attachment flushed in wall incl. mending good damages to original finish [only PVC casing-capping on ceiling and remaining portion concealed] | PWD/GS -E-23 : 8 (a)
Point Switch Board | Modular type | Casing-Capping | Only casing-capping on ceiling and remaining portion concealed | Average run 6 mtr | 907 |  | PWD/GS -E-23 : 8 (b)
Point Switch Board | Modular type | Casing-Capping | Only casing-capping on ceiling and remaining portion concealed | Average run 8 mtr | 1106 |  | PWD/GS -E-23 : 8 (c)
Point Switch Board | Modular type | Casing-Capping | Only casing-capping on ceiling and remaining portion concealed | Average run 9 mtr | 1206 |  | PWD/GS -E-23 : 8 (d)
Point Switch Board | Modular type | Casing-Capping | Only casing-capping on ceiling and remaining portion concealed | Average run 10 mtr | 1306 |  | PWD/GS -E-23 : 8 (e)
Point Switch Board | Modular type | Casing-Capping | Only casing-capping on ceiling and remaining portion concealed | Average run 11 mtr | 1405 |  | PWD/GS -E-23 : 8 (f)
Point Switch Board | Modular type | Casing-Capping | Only casing-capping on ceiling and remaining portion concealed | Average run 12 mtr | 1505 |  | PWD/GS -E-23 : 8 (g)
Point Switch Board | Modular type | Rigid Conduit | Conduit and board both on surface | Average run 5 mtr | 716 | Distribution wiring in 2 x 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in 20mm size PVC rigid conduit 'FR' (Precision make), with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, to light/fan/call bell points with Modular type switch (Brand approved by EIC) fixed on Modular GI switch board with top cover plate and 2 no. suitable size “Ph & N” copper bar & earthing attachment fixed on wall incl. mending good damages to original finish. | PWD/GS -E-24 : 1 (a)
Point Switch Board | Modular type | Rigid Conduit | Conduit and board both on surface | Average run 6 mtr | 801 |  | PWD/GS -E-24 : 1 (b)
Point Switch Board | Modular type | Rigid Conduit | Conduit and board both on surface | Average run 8 mtr | 970 |  | PWD/GS -E-24 : 1 (c)
Point Switch Board | Modular type | Rigid Conduit | Conduit and board both on surface | Average run 9 mtr | 1055 |  | PWD/GS -E-24 : 1 (d)
Point Switch Board | Modular type | Rigid Conduit | Conduit and board both on surface | Average run 10 mtr | 1140 |  | PWD/GS -E-24 : 1 (e)
Point Switch Board | Modular type | Rigid Conduit | Conduit and board both on surface | Average run 11 mtr | 1224 |  | PWD/GS -E-24 : 1 (f)
Point Switch Board | Modular type | Rigid Conduit | Conduit and board both on surface | Average run 12 mtr | 1309 |  | PWD/GS -E-24 : 1 (g)
Point Switch Board | Modular type | Rigid Conduit | Only Conduit on ceiling and remaining portion concealed | Average run 5 mtr | 775 | Distribution wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) partly in 20mm size PVC rigid conduit 'FR' (Precision make) [for ceiling portion only] and in 19mm bore, 3mm thick polythene pipe [for horizontal & vertical run embedded in wall], with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, to light/fan/call bell points with Modular type switch (Brand approved by EIC) fixed on Modular GI switch board complete with 2 no. suitable size “Ph & N” copper bar with top cover plate making earthing attachment fixed on wall incl. mending good damages to original finish. [only PVC Rigid Conduit on ceiling and remaining portion concealed] | PWD/GS -E-25 : 4 (a)
Point Switch Board | Modular type | Rigid Conduit | Only Conduit on ceiling and remaining portion concealed | Average run 6 mtr | 874 |  | PWD/GS -E-25 : 4 (b)
Point Switch Board | Modular type | Rigid Conduit | Only Conduit on ceiling and remaining portion concealed | Average run 8 mtr | 1074 |  | PWD/GS -E-25 : 4 (c)
Point Switch Board | Modular type | Rigid Conduit | Only Conduit on ceiling and remaining portion concealed | Average run 9 mtr | 1173 |  | PWD/GS -E-25 : 4 (d)
Point Switch Board | Modular type | Rigid Conduit | Only Conduit on ceiling and remaining portion concealed | Average run 10 mtr | 1273 |  | PWD/GS -E-25 : 4 (e)
Point Switch Board | Modular type | Rigid Conduit | Only Conduit on ceiling and remaining portion concealed | Average run 11 mtr | 1373 |  | PWD/GS -E-25 : 4 (f)
Point Switch Board | Modular type | Rigid Conduit | Only Conduit on ceiling and remaining portion concealed | Average run 12 mtr | 1472 |  | PWD/GS -E-25 : 4 (g)
Point Switch Board | Modular type | Rigid Conduit | Conduit only for horizontal run & above false ceiling and vertical run concealed | Average run 5 mtr | 844 | Distribution wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) partly in 20mm size PVC rigid conduit 'FR' (Precision make) [for horizontal run & above false ceiling portion only] and in 19mm bore, 3mm thick polythene pipe [for vertical run embedded in wall], with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, to light/fan/call bell points with Modular type switch (Brand approved by EIC) fixed on Modular GI switch board complete with 2 no. suitable size “Ph & N” copper bar with top cover plate making earthing attachment fixed on wall incl. mending good damages to original finish. [PVC Rigid Conduit only for horizontal run & above false ceiling and vertical run concealed] | PWD/GS -E-25 : 5 (a)
Point Switch Board | Modular type | Rigid Conduit | Conduit only for horizontal run & above false ceiling and vertical run concealed | Average run 6 mtr | 929 |  | PWD/GS -E-25 : 5 (b)
Point Switch Board | Modular type | Rigid Conduit | Conduit only for horizontal run & above false ceiling and vertical run concealed | Average run 8 mtr | 1100 |  | PWD/GS -E-25 : 5 (c)
Point Switch Board | Modular type | Rigid Conduit | Conduit only for horizontal run & above false ceiling and vertical run concealed | Average run 9 mtr | 1186 |  | PWD/GS -E-25 : 5 (d)
Point Switch Board | Modular type | Rigid Conduit | Conduit only for horizontal run & above false ceiling and vertical run concealed | Average run 10 mtr | 1271 |  | PWD/GS -E-25 : 5 (e)
Point Switch Board | Modular type | Rigid Conduit | Conduit only for horizontal run & above false ceiling and vertical run concealed | Average run 11 mtr | 1357 |  | PWD/GS -E-25 : 5 (f)
Point Switch Board | Modular type | Rigid Conduit | Conduit only for horizontal run & above false ceiling and vertical run concealed | Average run 12 mtr | 1442 |  | PWD/GS -E-25 : 5 (g)

## 13
Item | Type | Using | Wiring | Rate | Description | GS
On Board | Flush / Piano key | Polythen pipe | Embedded in wall | 76 | Distn. wiring in 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed single core stranded copper wire (Brand approved by EIC) in 19 mm bore, 3 mm thick polythen pipe complete with all accessories embedded in wall to 240 V 5A 3 pin plug point incl. S&F 240 V 5A 3 pin flush type plug socket & piano key type switch (Anchor make) incl. S&F earth continuity wire, fixed on sheet metal (16 SWG) switch board with bakelite/perspex (wall matching colour) top cover (3 mm thick) flushed in wall incl. mending good damages to original finish - 2x22/0.3 (Ph. & N) and 1x22/0.3 as ECC | PWD/GS -E-10 : 4 (a)(i)
On Board | Flush / Piano key | Casing-Capping | Casing-capping and board both on surface | 67 | Distribution Wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in suitable size PVC casing-capping (Precision make) with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, incl. necy. PVC clips, fittings etc. to 5A 3 pin flush type plug socket with piano key type switch (Anchor make) fixed on sheet steel fabricated CRC MS switch board with bakelite/perspex (wall matching color) top cover of 3 mm thick flushed in wall by housing the board after cutting brick wall incl. necy. connection making earthing attachment, painting and mending good damages to building works [PVC casing-capping and plug box both on surface] | PWD/GS -E-12 : 6 (a)
On Board | Flush / Piano key | Casing-Capping | Casing-capping on surface and board concealed | 67 | Distribution Wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in suitable size PVC casing-capping (Precision make) with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, incl. necy. PVC clips, fittings etc. to 5A 3 pin flush type plug socket with piano key type switch (Anchor make) fixed on sheet steel fabricated CRC MS switch board with bakelite/perspex (wall matching color) top cover of 3 mm thick flushed in wall by housing the board after cutting brick wall incl. necy. connection making earthing attachment, painting and mending good damages to building works [PVC casing-capping on surface and Switch board concealed] | PWD/GS -E-12 : 7 (a)
On Board | Flush / Piano key | Rigid Conduit | Conduit and board both on surface | 67 | Distribution wiring in 1.1 KV grade 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in 20mm size PVC rigid conduit 'FR' (Precision make), with 1.1 KV grade 1 x 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire as ECC, to 5A 3 pin flush type plug socket & Piano Key type switch fixed on MS CRC sheet metal (16 SWG) switch board cum JB on wall incl. bakelite/Perspex (wall matching color) top cover 3 mm thick and incl. painting the MS box and mending good the damages to original finish | PWD/GS -E-15 : 4 (a)
On Board | Modular type | Polythen pipe | Embedded in wall | 249 | Distn. wiring in 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed single core stranded copper wire (Brand approved by EIC) in 19 mm bore, 3 mm thick polythen pipe complete with all accessories embedded in wall to 240 V 6A 5 pin plug point incl. S&F 240 V 6A 3 pin Modular type plug socket & Modular type switch (Brand approved by EIC) incl. S&F earth continuity wire, fixed on 4 Module GI switch board with 3/4 Module top cover plate flushed in wall incl. mending good damages to original finish - 2x22/0.3 (Ph. & N) and 1x22/0.3 as ECC | PWD/GS -E-20 : 3 (i)
On Board | Modular type | Casing-Capping | Casing-capping and PVC board both on surface | 216 | Distribution Wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in suitable size PVC casing-capping (Precision make) with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, incl. necy. fittings etc. with S & F 6A 5 pin Modular type plug socket and switch (Brand approved by EIC) fixed on 4 Module PVC switch board with 3/4 Module top cover plate on wall incl. necy. connection making earthing attachment, painting and mending good damages to building works [PVC casing-capping and plug box both on surface] | PWD/GS -E-22 : 5 (a)
On Board | Modular type | Casing-Capping | Casing-capping and GI board both on surface | 216 | Distribution Wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in suitable size PVC casing-capping (Precision make) with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, incl. necy. fittings etc. with S & F 6A 5 pin Modular type plug socket and switch (Brand approved by EIC) fixed on 4 Module GI switch board with 3/4 Module top cover plate on wall incl. necy. connection making earthing attachment, painting and mending good damages to building works [PVC casing-capping and plug box both on surface] | PWD/GS -E-22 : 6 (a)
On Board | Modular type | Rigid Conduit | Conduit and board both on surface | 216 | Distribution wiring in 1.1 KV grade 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in 20mm size PVC rigid conduit 'FR' (Precision make), with 1.1 KV grade 1 x 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire as ECC, to 6A 3 pin Modular type plug socket & switch (Brand approved by EIC) on 4 Module GI switch board with 3/4 Module top cover plate on wall incl. necy. connection making earthing attachment, painting and mending good damages to building works. | PWD/GS -E-24 : 1 (a)

## 14
Item | Power | Type | Using | Wiring | Avg. Run | Rate | Description | GS
Avg. 5A Switch Board | 150 W | Flush / Piano key | Polythen pipe | Embedded in wall | Average run 1.5 mtr | 379 | Distn. wiring in 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed single core stranded copper wire (Brand approved by EIC) in 19 mm bore, 3 mm thick polythen pipe complete with all accessories embedded in wall to 240 V 5A 3 pin plug point incl. S&F 240 V 5A 3 pin flush type plug socket & piano key type switch (Anchor make) incl. S&F earth continuity wire, fixed on sheet metal (16 SWG) switch board with bakelite/perspex (wall matching colour) top cover (3 mm thick) flushed in wall incl. mending good damages to original finish - 2x22/0.3 (Ph. & N) and 1x22/0.3 as ECC | PWD/GS -E-10 : 4 (a)(ii)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Polythen pipe | Embedded in wall | Average run 3 mtr | 532 |  | PWD/GS -E-10 : 4 (a)(iii)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Polythen pipe | Embedded in wall | Average run 4.5 mtr | 684 |  | PWD/GS -E-10 : 4 (a)(iv)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Polythen pipe | Embedded in wall | Average run 6 mtr | 836 |  | PWD/GS -E-10 : 4 (a)(v)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Polythen pipe | Embedded in wall | Average run 7.5 mtr | 988 |  | PWD/GS -E-10 : 4 (a)(vi)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Casing-Capping | Casing-capping and board both on surface | Average run 1.5 mtr | 268 | Distribution Wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in suitable size PVC casing-capping (Precision make) with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, incl. necy. PVC clips, fittings etc. to 5A 3 pin flush type plug socket with piano key type switch (Anchor make) fixed on sheet steel fabricated CRC MS switch board with bakelite/perspex (wall matching color) top cover of 3 mm thick flushed in wall by housing the board after cutting brick wall incl. necy. connection making earthing attachment, painting and mending good damages to building works [PVC casing-capping and plug box both on surface] | PWD/GS -E-12 : 6 (b)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Casing-Capping | Casing-capping and board both on surface | Average run 3 mtr | 377 |  | PWD/GS -E-12 : 6 (c)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Casing-Capping | Casing-capping and board both on surface | Average run 4.5 mtr | 487 |  | PWD/GS -E-12 : 6 (d)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Casing-Capping | Casing-capping and board both on surface | Average run 6 mtr | 596 |  | PWD/GS -E-12 : 6 (e)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Casing-Capping | Casing-capping and board both on surface | Average run 7.5 mtr | 706 |  | PWD/GS -E-12 : 6 (f)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Casing-Capping | Casing-capping on surface and board concealed | Average run 1.5 mtr | 298 | Distribution Wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in suitable size PVC casing-capping (Precision make) with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, incl. necy. PVC clips, fittings etc. to 5A 3 pin flush type plug socket with piano key type switch (Anchor make) fixed on sheet steel fabricated CRC MS switch board with bakelite/perspex (wall matching color) top cover of 3 mm thick flushed in wall by housing the board after cutting brick wall incl. necy. connection making earthing attachment, painting and mending good damages to building works [PVC casing-capping on surface and Switch board concealed] | PWD/GS -E-12 : 7 (b)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Casing-Capping | Casing-capping on surface and board concealed | Average run 3 mtr | 408 |  | PWD/GS -E-12 : 7 (c)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Casing-Capping | Casing-capping on surface and board concealed | Average run 4.5 mtr | 517 |  | PWD/GS -E-12 : 7 (d)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Casing-Capping | Casing-capping on surface and board concealed | Average run 6 mtr | 627 |  | PWD/GS -E-12 : 7 (e)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Casing-Capping | Casing-capping on surface and board concealed | Average run 7.5 mtr | 736 |  | PWD/GS -E-12 : 7 (f)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Rigid Conduit | Conduit and board both on surface | Average run 1.5 mtr | 277 | Distribution wiring in 1.1 KV grade 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in 20mm size PVC rigid conduit 'FR' (Precision make), with 1.1 KV grade 1 x 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire as ECC, to 5A 3 pin flush type plug socket & Piano Key type switch fixed on MS CRC sheet metal (16 SWG) switch board cum JB on wall incl. bakelite/Perspex (wall matching color) top cover 3 mm thick and incl. painting the MS box and mending good the damages to original finish | PWD/GS -E-15 : 4 (b)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Rigid Conduit | Conduit and board both on surface | Average run 3 mtr | 405 |  | PWD/GS -E-15 : 4 (c)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Rigid Conduit | Conduit and board both on surface | Average run 4.5 mtr | 528 |  | PWD/GS -E-15 : 4 (d)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Rigid Conduit | Conduit and board both on surface | Average run 6 mtr | 651 |  | PWD/GS -E-15 : 4 (e)
Avg. 5A Switch Board | 150 W | Flush / Piano key | Rigid Conduit | Conduit and board both on surface | Average run 7.5 mtr | 775 |  | PWD/GS -E-15 : 4 (f)
Avg. 5A Switch Board | 150 W | Modular type | Polythen pipe | Embedded in wall | Average run 1.5 mtr | 639 | Distn. wiring in 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed single core stranded copper wire (Brand approved by EIC) in 19 mm bore, 3 mm thick polythen pipe complete with all accessories embedded in wall to 240 V 6A 5 pin plug point incl. S&F 240 V 6A 3 pin Modular type plug socket & Modular type switch (Brand approved by EIC) incl. S&F earth continuity wire, fixed on 4 Module GI switch board with 3/4 Module top cover plate flushed in wall incl. mending good damages to original finish - 2x22/0.3 (Ph. & N) and 1x22/0.3 as ECC | PWD/GS -E-20 : 3 (ii)
Avg. 5A Switch Board | 150 W | Modular type | Polythen pipe | Embedded in wall | Average run 3 mtr | 788 |  | PWD/GS -E-20 : 3 (iii)
Avg. 5A Switch Board | 150 W | Modular type | Polythen pipe | Embedded in wall | Average run 4.5 mtr | 938 |  | PWD/GS -E-20 : 3 (iv)
Avg. 5A Switch Board | 150 W | Modular type | Polythen pipe | Embedded in wall | Average run 6 mtr | 1087 |  | PWD/GS -E-20 : 3 (v)
Avg. 5A Switch Board | 150 W | Modular type | Polythen pipe | Embedded in wall | Average run 7.5 mtr | 1237 |  | PWD/GS -E-20 : 3 (vi)
Avg. 5A Switch Board | 150 W | Modular type | Casing-Capping | Casing-capping and PVC board both on surface | Average run 1.5 mtr | 478 | Distribution Wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in suitable size PVC casing-capping (Precision make) with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, incl. necy. fittings etc. with S & F 6A 5 pin Modular type plug socket and switch (Brand approved by EIC) fixed on 4 Module PVC switch board with 3/4 Module top cover plate on wall incl. necy. connection making earthing attachment, painting and mending good damages to building works [PVC casing-capping and plug box both on surface] | PWD/GS -E-22 : 5 (b)
Avg. 5A Switch Board | 150 W | Modular type | Casing-Capping | Casing-capping and PVC board both on surface | Average run 3 mtr | 588 |  | PWD/GS -E-22 : 5 (c)
Avg. 5A Switch Board | 150 W | Modular type | Casing-Capping | Casing-capping and PVC board both on surface | Average run 4.5 mtr | 697 |  | PWD/GS -E-22 : 5 (d)
Avg. 5A Switch Board | 150 W | Modular type | Casing-Capping | Casing-capping and PVC board both on surface | Average run 6 mtr | 807 |  | PWD/GS -E-22 : 5 (e)
Avg. 5A Switch Board | 150 W | Modular type | Casing-Capping | Casing-capping and PVC board both on surface | Average run 7.5 mtr | 916 |  | PWD/GS -E-22 : 5 (f)
Avg. 5A Switch Board | 150 W | Modular type | Casing-Capping | Casing-capping and GI board both on surface | Average run 1.5 mtr | 509 | Distribution Wiring in 1.1 KV grade 2x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in suitable size PVC casing-capping (Precision make) with 1x22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire for ECC, incl. necy. fittings etc. with S & F 6A 5 pin Modular type plug socket and switch (Brand approved by EIC) fixed on 4 Module GI switch board with 3/4 Module top cover plate on wall incl. necy. connection making earthing attachment, painting and mending good damages to building works [PVC casing-capping and plug box both on surface] | PWD/GS -E-22 : 6 (b)
Avg. 5A Switch Board | 150 W | Modular type | Casing-Capping | Casing-capping and GI board both on surface | Average run 3 mtr | 618 |  | PWD/GS -E-22 : 6 (c)
Avg. 5A Switch Board | 150 W | Modular type | Casing-Capping | Casing-capping and GI board both on surface | Average run 4.5 mtr | 728 |  | PWD/GS -E-22 : 6 (d)
Avg. 5A Switch Board | 150 W | Modular type | Casing-Capping | Casing-capping and GI board both on surface | Average run 6 mtr | 837 |  | PWD/GS -E-22 : 6 (e)
Avg. 5A Switch Board | 150 W | Modular type | Casing-Capping | Casing-capping and GI board both on surface | Average run 7.5 mtr | 947 |  | PWD/GS -E-22 : 6 (f)
Avg. 5A Switch Board | 150 W | Modular type | Rigid Conduit | Conduit and board both on surface | Average run 1.5 mtr | 454 | Distribution wiring in 1.1 KV grade 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in 20mm size PVC rigid conduit 'FR' (Precision make), with 1.1 KV grade 1 x 22/0.3 (1.5 sqmm) single core stranded 'FR' PVC insulated & unsheathed copper wire as ECC, to 6A 3 pin Modular type plug socket & switch (Brand approved by EIC) on 4 Module GI switch board with 3/4 Module top cover plate on wall incl. necy. connection making earthing attachment, painting and mending good damages to building works. | PWD/GS -E-24 : 1 (b)
Avg. 5A Switch Board | 150 W | Modular type | Rigid Conduit | Conduit and board both on surface | Average run 3 mtr | 547 |  | PWD/GS -E-24 : 1 (c)
Avg. 5A Switch Board | 150 W | Modular type | Rigid Conduit | Conduit and board both on surface | Average run 4.5 mtr | 633 |  | PWD/GS -E-24 : 1 (d)
Avg. 5A Switch Board | 150 W | Modular type | Rigid Conduit | Conduit and board both on surface | Average run 6 mtr | 719 |  | PWD/GS -E-24 : 1 (e)
Avg. 5A Switch Board | 150 W | Modular type | Rigid Conduit | Conduit and board both on surface | Average run 7.5 mtr | 805 |  | PWD/GS -E-24 : 1 (f)

## 15
Item | Type | Enclosure | Current Rating | Rate | Description | GS
End box for TPN SFU | TPN SFU | Sheet steel enclosure | 63A | 542 | Supplying and fixing sheet steel (16SWG) cable end box on TPN SFU enclosure with nuts bolts etc incl. powder coated painting.- 63/125A | PWD/GS -D-5 : 5
End box for TPN SFU | TPN SFU | Sheet steel enclosure | 80A | 542
End box for TPN SFU | TPN SFU | Sheet steel enclosure | 100A | 542
End box for TPN SFU | TPN SFU | Sheet steel enclosure | 125A | 542
End box for TPN SFU | TPN SFU | Sheet steel enclosure | 160A | 567 | Supplying and fixing sheet steel (16SWG) cable end box on TPN SFU enclosure with nuts bolts etc incl. powder coated painting.- 160/250A
End box for TPN SFU | TPN SFU | Sheet steel enclosure | 200A | 567
End box for TPN SFU | TPN SFU | Sheet steel enclosure | 250A | 567
End box for TPN SFU | TPN SFU | Sheet steel enclosure | 315A | 582 | Supplying and fixing sheet steel (16SWG) cable end box on TPN SFU enclosure with nuts bolts etc incl. powder coated painting.- 315/320A
End box for TPN SFU | TPN SFU | Sheet steel enclosure | 415A | 602 | Supplying and fixing sheet steel (16SWG) cable end box on TPN SFU enclosure with nuts bolts etc incl. powder coated painting.- 415A

## 16
Item | Type | Enclosure | Mounting | Current Rating | Voltage | Company | Rate | Description | GS
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 32A | 415V - TPN | Siemens | 2347 | Supplying and fixing following TPN SFU open execution in existing SS enclosure/cubical with nuts bolts etc incl. S & F 3 nos. DIN type HRC fuse as per rating. | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 32A | 415V - TPN | L&T | 1515 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 32A | 415V - TPN | Havells | 1454 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 32A | 415V - TPN | Standard | 1179 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 32A | 415V - TPN | ABB | 2257 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 50A | 415V - TPN | Siemens | 2831 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 63A | 415V - TPN | L&T | 2402 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 63A | 415V - TPN | Havells | 1979 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 63A | 415V - TPN | Standard | 1708 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 63A | 415V - TPN | ABB | 2867 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 80A | 415V - TPN | Siemens | 4503 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 100A | 415V - TPN | Siemens | 5433 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 100A | 415V - TPN | L&T | 4253 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 100A | 415V - TPN | Havells | 4180 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 100A | 415V - TPN | Standard | 3525 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 100A | 415V - TPN | ABB | 5242 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 125A | 415V - TPN | Siemens | 7019 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 125A | 415V - TPN | L&T | 5440 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 125A | 415V - TPN | Havells | 4740 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 125A | 415V - TPN | Standard | 3704 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 125A | 415V - TPN | ABB | 6815 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 160A | 415V - TPN | Siemens | 7600 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 160A | 415V - TPN | L&T | 6001 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 160A | 415V - TPN | Havells | 5586 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 160A | 415V - TPN | Standard | 4446 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 160A | 415V - TPN | ABB | 7494 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 200A | 415V - TPN | Siemens | 9832 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 200A | 415V - TPN | L&T | 7602 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 200A | 415V - TPN | Havells | 6511 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 200A | 415V - TPN | ABB | 9170 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 250A | 415V - TPN | Siemens | 11546 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 250A | 415V - TPN | L&T | 9084 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 250A | 415V - TPN | Havells | 7368 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 250A | 415V - TPN | Standard | 6065 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 250A | 415V - TPN | ABB | 11150 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 315A | 415V - TPN | Siemens | 14402 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 315A | 415V - TPN | L&T | 10975 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 315A | 415V - TPN | Havells | 10106 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 315A | 415V - TPN | Standard | 7931 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 315A | 415V - TPN | ABB | 15970 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 415A | 415V - TPN | Siemens | 17026 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 415A | 415V - TPN | L&T | 13255 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 415A | 415V - TPN | Havells | 12822 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 415A | 415V - TPN | Standard | 9432 |  | PWD/GS -D-4 : 4(b)
Main Switch Open | TPN SFU | open execution type | in existing SS enclosure/cubical | 415A | 415V - TPN | ABB | 16198 |  | PWD/GS -D-4 : 4(b)

## 17
Item | Type | Mounting | Current Rating | Voltage | Company | Rate | Description | GS
Change Over Switch Open | open execution type | in SS enclosure/cubical | 125A | 415V FP | L&T | 6321 | Supplying and fixing following on load front operated Changeover switch open execution type in SS enclosure/cubical with nuts bolts etc | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 125A | 415V FP | Havells | 6950 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 125A | 415V FP | HPL | 7077 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 125A | 415V FP | Standard | 6751 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 160A | 415V FP | L&T | 6969 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 160A | 415V FP | Havells | 7570 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 160A | 415V FP | HPL | 7730 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 160A | 415V FP | Standard | 7352 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 200A | 415V FP | L&T | 8385 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 200A | 415V FP | Havells | 9002 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 200A | 415V FP | HPL | 9305 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 200A | 415V FP | Standard | 8743 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 250A | 415V FP | L&T | 11808 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 250A | 415V FP | Havells | 13287 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 250A | 415V FP | HPL | 13370 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 250A | 415V FP | Standard | 12902 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 320A | 415V FP | L&T | 12404 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 320A | 415V FP | Havells | 14235 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 320A | 415V FP | HPL | 14110 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 320A | 415V FP | Standard | 13824 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 415A | 415V FP | L&T | 18378 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 415A | 415V FP | Havells | 20660 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 415A | 415V FP | HPL | 20562 |  | PWD/GS -D-2 : 3(b)
Change Over Switch Open | open execution type | in SS enclosure/cubical | 415A | 415V FP | Standard | 20062 |  | PWD/GS -D-2 : 3(b)

## 18
Item | Way | Rate | Description | GS
End box for Vertical TPN DB | 4 way | 1072 | Supplying and fixing double door sheet steel (16SWG), powder coated cable end box for TPN DB vertical enclosure with IP-42/43 protection, on angle iron frame on wall & mending good the damages to original finish with nuts bolts etc incl. provision for earthing attachment | PWD/GS -D-12 : 16
End box for Vertical TPN DB | 6 way | 1072
End box for Vertical TPN DB | 8 way | 1072
End box for Vertical TPN DB | 12 way | 1072

## 19
Item | Way | Rate | Description | GS
End box for Horizontal TPN DB | 4 way | 682 | Supplying and fixing double door sheet steel (16SWG), powder coated cable end box for TPN DB Horizontal enclosure with IP-42/43 protection, on angle iron frame on wall & mending good the damages to original finish with nuts bolts etc incl. provision for earthing attachment | PWD/GS -D-12 : 16
End box for Horizontal TPN DB | 6 way | 682
End box for Horizontal TPN DB | 8 way | 836
End box for Horizontal TPN DB | 12 way | 1105

## 20
Item | Armoured | Core | Size | Rate | Description | GS
Compression Glands | Armoured | 2 Core | 4 sq.mm. | 63 | Supplying and fixing compression type gland complete with brass gland, brass ring & rubber ring for dust & moisture-proof entry of XLPE/PVC armoured cables as below : | PWD/GS -F-4 : 7(a)
Compression Glands | Armoured | 2 Core | 6 sq.mm. | 68
Compression Glands | Armoured | 2 Core | 10 sq.mm. | 115
Compression Glands | Armoured | 2 Core | 16 sq.mm. | 115
Compression Glands | Armoured | 2 Core | 25 sq.mm. | 132
Compression Glands | Armoured | 2 Core | 35 sq.mm. | 162
Compression Glands | Armoured | 2 Core | 50 sq.mm. | 177
Compression Glands | Armoured | 3 Core | 4 sq.mm. | 115 |  | PWD/GS -F-4 : 7(b)
Compression Glands | Armoured | 3 Core | 6 sq.mm. | 115
Compression Glands | Armoured | 3 Core | 10 sq.mm. | 115
Compression Glands | Armoured | 3 Core | 16 sq.mm. | 132
Compression Glands | Armoured | 3 Core | 25 sq.mm. | 152
Compression Glands | Armoured | 3 Core | 35 sq.mm. | 162
Compression Glands | Armoured | 3 Core | 50 sq.mm. | 197
Compression Glands | Armoured | 3 Core | 70 sq.mm. | 212
Compression Glands | Armoured | 3 Core | 95 sq.mm. | 234
Compression Glands | Armoured | 3 Core | 120 sq.mm. | 274
Compression Glands | Armoured | 3 Core | 150 sq.mm. | 307
Compression Glands | Armoured | 3 Core | 185 sq.mm. | 355
Compression Glands | Armoured | 3 Core | 240 sq.mm. | 430
Compression Glands | Armoured | 3 Core | 300 sq.mm. | 478
Compression Glands | Armoured | 3 Core | 400 sq.mm. | 556
Compression Glands | Armoured | 3.5 Core | 25 sq.mm. | 152 |  | PWD/GS -F-4 : 7(d)
Compression Glands | Armoured | 3.5 Core | 35 sq.mm. | 162
Compression Glands | Armoured | 3.5 Core | 50 sq.mm. | 197
Compression Glands | Armoured | 3.5 Core | 70 sq.mm. | 212
Compression Glands | Armoured | 3.5 Core | 95 sq.mm. | 274
Compression Glands | Armoured | 3.5 Core | 120 sq.mm. | 274
Compression Glands | Armoured | 3.5 Core | 150 sq.mm. | 307
Compression Glands | Armoured | 3.5 Core | 185 sq.mm. | 394
Compression Glands | Armoured | 3.5 Core | 240 sq.mm. | 430
Compression Glands | Armoured | 3.5 Core | 300 sq.mm. | 517
Compression Glands | Armoured | 3.5 Core | 400 sq.mm. | 556
Compression Glands | Armoured | 4 Core | 4 sq.mm. | 115 |  | PWD/GS -F-4 : 7(c)
Compression Glands | Armoured | 4 Core | 6 sq.mm. | 115
Compression Glands | Armoured | 4 Core | 10 sq.mm. | 132
Compression Glands | Armoured | 4 Core | 16 sq.mm. | 132
Compression Glands | Armoured | 4 Core | 25 sq.mm. | 162
Compression Glands | Armoured | 4 Core | 35 sq.mm. | 162
Compression Glands | Armoured | 4 Core | 50 sq.mm. | 197
Compression Glands | Armoured | 4 Core | 70 sq.mm. | 212
Compression Glands | Armoured | 4 Core | 95 sq.mm. | 234
Compression Glands | Armoured | 4 Core | 120 sq.mm. | 307
Compression Glands | Armoured | 4 Core | 150 sq.mm. | 355
Compression Glands | Armoured | 4 Core | 185 sq.mm. | 391
Compression Glands | Armoured | 4 Core | 240 sq.mm. | 478
Compression Glands | Armoured | 4 Core | 300 sq.mm. | 516
Compression Glands | Armoured | 4 Core | 400 sq.mm. | 629

## 21
Item | Conduit | Conduit size | Conductor Size | Rate | Description | GS
Wiring | Prelaid | Any | 2 x 1.5 sq.mm | 34 | Supplying and Drawing 1.1 KV single core stranded 'FR' PVC insulated & unsheathed single core stranded copper wire (Brand approved by EIC) of the following sizes in the prelaid polythene pipe and by the prelaid GI fish wire and making necy. connection as required | PWD/GS -E-9 : 1
Wiring | Prelaid | Any | 3 x 1.5 sq.mm | 48
Wiring | Prelaid | Any | 4 x 1.5 sq.mm | 65
Wiring | Prelaid | Any | 2 x 2.5 sq.mm | 51
Wiring | Prelaid | Any | 3 x 2.5 sq.mm | 74
Wiring | Prelaid | Any | 4 x 2.5 sq.mm | 100
Wiring | Prelaid | Any | 2 x 4 sq.mm | 72
Wiring | Prelaid | Any | 3 x 4 sq.mm | 106
Wiring | Prelaid | Any | 4 x 4 sq.mm | 142
Wiring | Prelaid | Any | 2 x 6 sq.mm | 106
Wiring | Prelaid | Any | 3 x 6 sq.mm | 156
Wiring | Prelaid | Any | 4 x 6 sq.mm | 209
Wiring | Prelaid | Any | 2 x 10 sq.mm | 198
Wiring | Prelaid | Any | 3 x 10 sq.mm | 294
Wiring | Prelaid | Any | 4 x 10 sq.mm | 393
Wiring | Prelaid | Any | 2 x 16 sq.mm | 303
Wiring | Prelaid | Any | 3 x 16 sq.mm | 452
Wiring | Prelaid | Any | 4 x 16 sq.mm | 603
Wiring | Prelaid | Any | 2 x 2.5 + 1 x 1.5 sq.mm | 65
Wiring | Prelaid | Any | 3 x 2.5 + 2 x 1.5 sq.mm | 105
Wiring | Prelaid | Any | 4 x 2.5 + 2 x 1.5 sq.mm | 128
Wiring | Prelaid | Any | 2 x 4 + 1 x 2.5 sq.mm | 95
Wiring | Prelaid | Any | 3 x 4 + 2 x 2.5 sq.mm | 154
Wiring | Prelaid | Any | 4 x 4 + 2 x 2.5 sq.mm | 187
Wiring | Prelaid | Any | 2 x 6 + 1 x 4 sq.mm | 139
Wiring | Prelaid | Any | 3 x 6 + 2 x 4 sq.mm | 226
Wiring | Prelaid | Any | 4 x 6 + 2 x 4 sq.mm | 276
Wiring | Prelaid | Any | 4 x 10 + 1 x 6 sq.mm | 248
Wiring | Prelaid | Any | 2 x 10 + 2 x 6 sq.mm | 397
Wiring | Prelaid | Any | 3 x 10 + 2 x 6 sq.mm | 493
Wiring | Prelaid | Any | 2 x 16 + 1 x 10 sq.mm | 399
Wiring | Prelaid | Any | 3 x 16 + 2 x 10 sq.mm | 647
Wiring | Prelaid | Any | 4 x 16 + 2 x 10 sq.mm | 795
Wiring | Casing-Capping | 25mm | 2 x 1.5 sq.mm | 71 | Wiring in 1.1 KV grade single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) of following sizes in 25mm PVC casing-capping (Precision make) incl. necy. PVC clips, fittings etc. | PWD/GS -E-11 : D1
Wiring | Casing-Capping | 25mm | 3 x 1.5 sq.mm | 85
Wiring | Casing-Capping | 25mm | 2 x 2.5 + 1 x 1.5 sq.mm | 102
Wiring | Casing-Capping | 25mm | 2 x 4 + 1 x 1.5 sq.mm | 123
Wiring | Casing-Capping | 25mm | 2 x 4 + 1 x 2.5 sq.mm | 132
Wiring | Rigid Conduit | 20mm | 3 x 1.5 sq.mm | 102 | Distribution wiring in 1.1 KV single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in 20mm size PVC rigid conduit 'FR' (Precision make) incl. necy. fittings as required | PWD/GS -E-14 : E1(a)
Wiring | Rigid Conduit | 20mm | 2 x 2.5 + 1 x 1.5 sq.mm | 119
Wiring | Rigid Conduit | 20mm | 2 x 4 + 1 x 2.5 sq.mm | 149
Wiring | Rigid Conduit | 20mm | 2 x 6 + 1 x 4 sq.mm | 193
Wiring | Rigid Conduit | 20mm | 4 x 1.5 sq.mm | 116
Wiring | Rigid Conduit | 20mm | 3 x 2.5 + 2 x 1.5 sq.mm | 156
Wiring | Rigid Conduit | 25mm | 3 x 4 + 2 x 2.5 sq.mm | 219 | Distribution wiring in 1.1 KV single core stranded 'FR' PVC insulated & unsheathed copper wire (Brand approved by EIC) in 25mm size PVC rigid conduit 'FR' (Precision make) incl. necy. fittings as required | PWD/GS -E-14 : E1(b)
Wiring | Rigid Conduit | 25mm | 4 x 2.5 + 2 x 1.5 sq.mm | 192
Wiring | Rigid Conduit | 25mm | 4 x 4 + 2 x 2.5 sq.mm | 252
Wiring | Rigid Conduit | 25mm | 3 x 6 + 2 x 4 sq.mm | 290
Wiring | Rigid Conduit | 25mm | 4 x 6 + 2 x 4 sq.mm | 340
Wiring | Polythen pipe | 19mm | 2 x 2.5 + 1 x 1.5 sq.mm | 162 | Distn. wiring with 2 x 36/0.3 (2.5 sqmm) single core stranded copper conductor PVC insulated and unsheathed copper wire (Brand approved by EIC) in 19mm dia 3 mm thick polythene pipe with 1x22/0.3 (1.5sqmm) PVC insulated and unsheathed coper wire as ECC, complete with all accessories embedded in wall | PWD/GS -E-10 : 5

## 22
Size (mm²) | Laid in Ground - Single Core (Amps) | Laid in Ground - Twin Core (Amps) | Laid in Ground - 3/3.5/4 Core (Amps) | In Single Way Duct - Single Core (Amps) | In Single Way Duct - Twin Core (Amps) | In Single Way Duct - 3/3.5/4 Core (Amps) | In Air - Single Core (Amps) | In Air - Twin Core (Amps) | In Air - 3/3.5/4 Core (Amps)
1.5 | 20 | 21 | 18 | 20 | 18 | 16 | 18 | 20 | 16
2.5 | 28 | 29 | 24 | 28 | 24 | 21 | 26 | 26 | 22
4 | 36 | 37 | 33 | 35 | 32 | 27 | 33 | 34 | 28
6 | 46 | 47 | 41 | 43 | 40 | 35 | 43 | 43 | 37
10 | 60 | 64 | 54 | 60 | 53 | 46 | 57 | 57 | 49
16 | 77 | 82 | 70 | 76 | 68 | 59 | 77 | 72 | 61
25 | 101 | 105 | 89 | 97 | 89 | 74 | 102 | 95 | 85
35 | 117 | 129 | 108 | 117 | 108 | 90 | 127 | 121 | 105
50 | 140 | 158 | 119 | 135 | 135 | 111 | 159 | 153 | 128
70 | 164 | 187 | 158 | 158 | 164 | 135 | 189 | 183 | 159
95 | 205 | 222 | 193 | 181 | 199 | 164 | 232 | 226 | 189
120 | 228 | 246 | 216 | 199 | 222 | 183 | 268 | 256 | 220
150 | 256 | 280 | 246 | 222 | 246 | 205 | 305 | 292 | 250
185 | 280 | 322 | 275 | 246 | 281 | 234 | 354 | 336 | 293
225 | 304 | 357 | 304 | 258 | 304 | 258 | 390 | 372 | 302
240 | 316 | 374 | 322 | 264 | 322 | 275 | 409 | 397 | 342
300 | 345 | 415 | 357 | 286 | 357 | 304 | 464 | 445 | 384
400 | 380 | 450 | 392 | 322 | 404 | 340 | 531 | 513 | 458
500 | 403 |  | 427 | 345 |  | 368 | 586 |  | 513
625 | 456 |  | 462 | 374 |  | 398 | 671 |  | 586

## 23
Size (mm²) | Laid in Ground - Single Core (Amps) | Laid in Ground - Twin Core (Amps) | Laid in Ground - 3/3.5/4 Core (Amps) | In Single Way Duct - Single Core (Amps) | In Single Way Duct - Twin Core (Amps) | In Single Way Duct - 3/3.5/4 Core (Amps) | In Air - Single Core (Amps) | In Air - Twin Core (Amps) | In Air - 3/3.5/4 Core (Amps)
1.5 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17
2.5 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24
4 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 30
6 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 39
10 | 71 | 65 | 65 | 71 | 65 | 65 | 71 | 65 | 52
16 | 95 | 87 | 87 | 95 | 87 | 87 | 95 | 87 | 66
25 | 125 | 115 | 115 | 125 | 115 | 115 | 125 | 115 | 90
35 | 150 | 138 | 138 | 150 | 138 | 138 | 150 | 138 | 110
50 | 175 | 161 | 161 | 175 | 161 | 161 | 175 | 161 | 135
70 | 220 | 202 | 202 | 220 | 202 | 202 | 220 | 202 | 165
95 | 260 | 239 | 239 | 260 | 239 | 239 | 260 | 239 | 200
120 | 301 | 276 | 276 | 301 | 276 | 276 | 301 | 276 | 235
150 | 336 | 308 | 308 | 336 | 308 | 308 | 336 | 308 | 265
185 | 381 | 350 | 350 | 381 | 350 | 350 | 381 | 350 | 305
225 | 420 | 380 | 380 | 420 | 380 | 380 | 420 | 380 | 320
240 | 441 | 405 | 405 | 441 | 405 | 405 | 441 | 405 | 355
300 | 496 | 455 | 455 | 496 | 455 | 455 | 496 | 455 | 400
400 | 586 | 538 | 538 | 586 | 538 | 538 | 586 | 538 | 455

## 24
Size (mm²) | Current Carrying Capacity ( Amp)
1.5 | 17
2.5 | 24
4 | 32
6 | 41
10 | 57
16 | 76
25 | 101
35 | 125
50 | 151

## 25
Aluminium Size (mm²) | In Air – (mV/A/m)
1 | 31.971
1.5 | 22.134
2.5 | 13.444
4 | 8.362
6 | 5.574
10 | 3.361
16 | 2.099
25 | 1.344
35 | 0.951
50 | 0.721
70 | 0.508
95 | 0.377
120 | 0.312
150 | 0.246
185 | 0.213
225 | 0.172
240 | 0.159
300 | 0.125
400 | 0.093

## 26
Copper Size (mm²) | In Air – (mV/A/m)
1 | 19.5
1.5 | 13.5
2.5 | 8.2
4 | 5.1
6 | 3.4
10 | 2.05
16 | 1.28
25 | 0.82
35 | 0.58
50 | 0.44
70 | 0.31
95 | 0.23
120 | 0.19
150 | 0.15
185 | 0.13
225 | 0.105
240 | 0.097
300 | 0.076
400 | 0.057